CALIFORNIA REGIONAL WATER QUALITY CONTROL BOARD

SAN DIEGO REGION

ORDER NO. 2000-12

NPDES NO. CA0108031

WASTE DISCHARGE REQUIREMENTS

FOR THE

FALLBROOK PUBLIC UTILITY DISTRICT

WASTEWATER TREATMENT PLANT NO. 1

DISCHARGE TO THE PACIFIC OCEAN

VIA THE OCEANSIDE OCEAN OUTFALL

Table of Contents

Findings									2

- Prohibitions									10

- Discharge Specifications							12

- Receiving Water Limitations							19

- Pretreatment Requirements							26

- Sludge Requirements								26

- Provisions									29

- Reporting Requirements							39

- Notifications									47

- Order No. 2000-12 Endnotes							48

- Attachment No. 1 (1997 Ocean Plan Discharge Prohibitions)		50

- Attachment No. 2 (Basin Plan Waste Discharge Prohibitions)		51

- Attachment No. 3 (40 CFR Standard Provision References)			53

- Attachment No. 4 (Region 9 Standard Provisions)				99

- Attachment No. 5 (Regional Board Contact Information)			104

- Monitoring and Reporting Program No. 2000-12				105

- Purpose								105

- Monitoring Provisions						105

- Influent Monitoring							108

- Effluent Monitoring							108

- Solids Monitoring							112

- Receiving Water Monitoring						112

- Monitoring and Reporting Program Endnotes			120

CALIFORNIA REGIONAL WATER QUALITY CONTROL BOARD

SAN DIEGO REGION

ORDER NO. 2000-12

NPDES NO. CA0108031

WASTE DISCHARGE REQUIREMENTS

FOR THE

FALLBROOK PUBLIC UTILITY DISTRICT

WASTEWATER TREATMENT PLANT NO. 1

DISCHARGE TO THE PACIFIC OCEAN

VIA THE OCEANSIDE OCEAN OUTFALL

The California Regional Water Quality Control Board, San Diego Region (hereinafter referred to as Regional Board) finds that:

1.	On July 18, 1983, this Regional Board adopted Order No. 83-19, NPDES No. CA0108031, Waste Discharge Requirements for Fallbrook Sanitary District, San Diego County.  Order No. 83-19, and Addenda Nos. 1, 2, and 3 thereto, established requirements for the combined discharge of up to 1.95 million gallons per day (MGallons/Day) of treated wastewater from the Fallbrook Sanitary District Water Pollution Control Facility Plant Nos. 1 and 2 to the Pacific Ocean through the Oceanside Ocean Outfall.  Order No. 83-19 contained an expiration date of July 18, 1988.

2.	On February 27, 1989, this Regional Board adopted Order No. 89-13, NPDES No. CA0108031, Waste Discharge Requirements for the Fallbrook Sanitary District Water Pollution Control Facilities Plant Nos. 1 and 2 Discharge Through The Oceanside Ocean Outfall, San Diego County.  Order No. 89-13 established requirements for the combined discharge of up to 3.1 MGallons/Day of treated wastewater from the Fallbrook Sanitary District Water Pollution Control Facility Plant Nos. 1 and 2 to the Pacific Ocean through the Oceanside Ocean Outfall.  Order No. 89-13 contained an expiration date of February 27, 1994.

3.	Monitoring and Reporting Program No. 83-19 remained in effect with the adoption of Order No. 89-13, as no new monitoring and reporting program was issued with Order No. 89-13.

4.	On January 26, 1995, the Fallbrook Public Utility District submitted a letter notifying the Regional Board that the Fallbrook Sanitary District had merged with the Fallbrook Public Utility District.  The Fallbrook Public Utility District has been responsible for permit conditions since the transfer date of December 20, 1994.

5.	On February 9, 1995, this Regional Board adopted Order No. 95-08, NPDES No. CA0108031, Waste Discharge Requirements for the Fallbrook Public Utility District Discharge to the Pacific Ocean Through The Fallbrook Land Outfall and the Oceanside Ocean Outfall.  Order No. 95-08 established requirements for the combined discharge of up to 3.1 MGallons/Day of treated wastewater from the Fallbrook Public Utility District Water Pollution Control Facility Plant Nos. 1 and 2 to the Pacific Ocean through the Oceanside Ocean Outfall.  Order No. 95-08 contained an expiration date of February 9, 2000.

6.	On June 8, 1995, this Regional Board adopted Technical Change Order No. 1 to Monitoring and Reporting Program No. 95-08 for the Fallbrook Public Utility District Discharge Through the Oceanside Ocean Outfall, which became effective on July 1, 1995.

7.	On August 12, 1999, the Fallbrook Public Utility District submitted an application for the renewal of its NPDES permit pursuant to Reporting Requirement No. E.1 of Order No. 95-08.  Upon adoption, this Order will supersede Order No. 95-08 and will serve as the renewal of Order No. 95-08 after its expiration on February 9, 2000.

8.	The Fallbrook Public Utility District (FPUD) provides for the collection, treatment, and disposal of wastewater generated in the town of Fallbrook.  The FPUD owns and operates two wastewater treatment plants.  In its application for permit renewal submitted on August 12, 1999, FPUD reported that Treatment Plant No. 2 was in the final stages of its conversion to a lift station, and would no longer be used as a wastewater treatment facility.  In addition to the report of the cessation of treatment at Treatment Plant No. 2, FPUD provided in their August 12, 1999 Report of Waste Discharge only information for the treatment processes occurring at Treatment Plant No. 1.  This permit, therefore, only applies Waste Discharge Requirements to the effluent and biosolids resulting from the treatment processes occurring at Treatment Plant No. 1.

9.	Wastewater Treatment Plant No. 2 is located at 2858 Overland Trail in Fallbrook, adjacent to Ostrich Creek.

10.	Wastewater treatment unit operations and processes at Wastewater Treatment Plant No. 2 formerly consisted of preliminary treatment by screening, comminution, and secondary treatment using an activated sludge contact stabilization process followed by secondary clarification.  All of the wastewater received by Treatment Plant No. 2 will be pumped to the headworks of Treatment Plant No. 1 for treatment.

11.	Treatment Plant No. 1 is located at 1425 South Alturas in Fallbrook, adjacent to Fallbrook Creek.

12.	Wastewater treatment unit operations and processes at Treatment Plant No. 1 consist of preliminary treatment by screening, grit removal, primary sedimentation, biological treatment using activated sludge followed by secondary clarification, tertiary treatment by flocculation and sand filtration, and chlorination.  Treated wastewater is discharged to the Pacific Ocean through the Oceanside Ocean Outfall (OOO) via the Fallbrook Land Outfall (FLO).  It is common for all of the effluent entering the FLO to have received tertiary treatment at Treatment Plant No. 1.  Sludge is aerobically digested, then dewatered by a belt press.  If the belt press is inoperative, sludge is dewatered in sludge drying beds.  Final sludge disposal is currently by compost, reuse, or landfill.

13.	The secondary treatment design capacity of Treatment Plant No. 1 is 2.7 MGallons/Day.  The design capacity of the tertiary treatment facilities at Treatment Plant No. 1 is 3.1 MGallons/Day.  Monthly monitoring reports for 1998 and from January to September 1999 indicated that the average flowrate from Treatment Plant No. 1 was approximately 1.5 MGallons/Day, representing 56% of the design capacity of the facility.

14.	The permitted flowrate of 3.1 MGallons/Day authorized in Order No. 95-08 was based on the combined design flowrates from Treatment Plant Nos. 1 (2.7 MGallons/Day) and 2 (0.4 MGallons/Day).  As Treatment Plant No. 2 will no longer be permitted as a wastewater treatment facility, its design flow will no longer be considered as part of FPUD treatment capacity.  This Order, therefore, authorizes the discharge of an average dry weather flowrate of 2.7 MGallons/Day from FPUD Treatment Plant No. 1 to the Pacific Ocean through the Oceanside Ocean Outfall.

15.	The FPUD discharge of reclaimed water for beneficial use is regulated by this Regional Board's Order No. 91-39, Waste Discharge Requirements for Fallbrook Sanitary District Plant Nos. 1 and 2, Reclamation Projects, San Diego County.

16.   	Effluent from Treatment Plant No. 1 is discharged to the Pacific Ocean through the OOO via the FLO.  The FPUD has a contract with the City of Oceanside for the discharge of an average annual flowrate of 2.4 MGallons/Day of treated wastewater from Treatment Plant No. 1 through the OOO, which is owned by the City of Oceanside, via the Fallbrook Land Outfall (FLO) and the Oceanside Land Outfall (OLO).  The discharge from the City of Oceanside through the OOO is regulated by a separate NPDES permit, Order No. 95-07 (NPDES No. CA0107433), which is scheduled for renewal on February 9, 2000 as Order No. 2000-11.

17.	The OOO extends southwesterly from the mouth of Loma Alta Creek in the City of Oceanside.  The inshore end of the diffuser is located approximately 8,050 feet offshore at a depth of approximately 102 feet.  The diffuser, which is collinear with the rest of the outfall, is approximately 230 feet long and extends to a depth of approximately 108 feet.  The terminus of the diffuser is located at Latitude 33o 09' 46" North, Longitude 117o 23' 28" West.

18.	The design capacity of the OOO is 30 MGallons/Day (average daily flow), with a maximum rated peak day capacity of 45 MGallons/Day.  Based on characteristics of the OOO, State Water Resources Control Board (SWRCB) staff has determined the minimum initial dilution for the OOO to be 82, using the computer model UMERGE.  This determination was based in part on the following characteristics of the ocean outfall diffuser system.

| Outfall Characteristic | Value |
| --- | --- |
| Outfall Flowrate | 21.3 MGallons/Day* |
| Length of Diffuser | 230 Feet |
| Number of Ports | 24 |
| Port Spacing | 10 Feet |
| Port Diameters | Ten 4" Ports and Fourteen 5" Ports |
| Port Angle From Horizontal (horizontal = 0, vertical = 90) | 0 |
| Average Port Depth | 100 Feet |

*  3.1 MGallons/Day from Treatment Plant Nos. 1 and 2, and 18.2 MGallons/Day from the City of Oceanside La Salina and San Luis Rey Wastewater Treatment Plants and Brackish Groundwater Desalinization Facility

19.	The SWRCB adopted a revised Water Quality Control Plan for Ocean Waters of California (California Ocean Plan) on July 23, 1997.  The Ocean Plan identifies the following beneficial uses of state ocean waters to be protected:

a.	Industrial water supply

b.	Navigation

c.	Water contact recreation

- Non-contact water recreation

- Ocean commercial and sport fishing

- Preservation and enhancement of Areas of Special Biological Significance

g.	Preservation of rare and endangered species

h.	Marine habitat

- Mariculture

- Fish migration

k.	Fish spawning

- Shellfish harvesting

m.	Aesthetic enjoyment

In order to protect these beneficial uses, the Ocean Plan establishes water quality objectives (for bacterial, physical, chemical, and biological characteristics, and for radioactivity), general requirements for management of waste discharge to the ocean, quality requirements for waste discharges (effluent water quality requirements), discharge prohibitions, and general provisions.

20.	The Comprehensive Water Quality Control Plan Report, San Diego Basin (9), (Basin Plan) was adopted by this Regional Board on March 17, 1975 and subsequently approved by the SWRCB.  Subsequent revisions to the Basin Plan have also been adopted by the Regional Board and approved by the SWRCB.  At the time of preparation of this Order, the most recent revisions to the Basin Plan were dated September 8, 1994.

21.	The Basin Plan identifies the following beneficial uses of state ocean waters to be protected:

a.	Industrial service supply

b.	Navigation

c.	Water contact recreation

d.	Non-contact water recreation

e.	Ocean commercial and sport fishing

f.	Preservation of Areas of Special Biological Significance (ASBS)

g.	Preservation of rare and endangered species

h.	Marine habitat

i.	Mariculture

j.	Fish migration

k.	Fish spawning

l.	Shellfish harvesting

m.	Wildlife habitat

The Basin Plan relies primarily on the requirements of the Ocean Plan for protection of these beneficial uses.  The Basin Plan, however, establishes additional water quality objectives for dissolved oxygen and pH.

22.	The 1997 Ocean Plan states that, “Water shall not be discharged to areas designated as being of special biological significance.  Discharges shall be located a sufficient distance from such designated areas to assure maintenance of natural water quality conditions in that area.”

23.	Oceanside Artificial Fishing Reef No. 1, described in the California Department of Fish and Game Guide to Artificial Reefs of Southern California, is located approximately 6,000 feet north of the inshore end of the OOO diffuser at Latitude 33 10' 57" North, Longitude 117 25' 00" West.

24.	Receiving Water Limitation No. C.1.a. (2) of this Order establishes bacterial objectives for areas where shellfish may be harvested for human consumption, as determined by the Regional Board.  As of the date of adoption of this Order, however, this Regional Board has not designated any shellfish harvesting area.  If and when this Regional Board, in consultation with the Department of Fish and Game, health agencies, and other interested parties, does designate shellfish harvesting areas in the vicinity of this discharge, this Order will be amended to identify the area(s) to which Receiving Water Limitation No. C.1.a. (2) applies.

25.	Federal regulations (40 CFR Part 403) establish pretreatment program requirements for POTWs which receive pollutants from industries subject to pretreatment standards.  As FPUD Treatment Plant No. 1 does not currently receive pollutants from any industry subject to pretreatment standards, and other circumstances do not currently warrant a pretreatment program, the FPUD is not required to have an industrial pretreatment program at this time.  However, this Order requires the FPUD to conduct an annual survey to determine if FPUD Treatment Plant No. 1 receives pollutants from any industry which is subject to pretreatment standards and to submit an annual certification report based on that survey (See Pretreatment Requirements, Section D.).  The Regional Board may amend this Order, at any time, to require the discharger to establish an industrial pretreatment program pursuant to the requirements of 40 CFR Part 403, if the Regional Board finds that FPUD Treatment Plant No. 1 receives pollutants from an industry which is subject to pretreatment standards or if other circumstances warrant doing so.

26.	On November 16, 1990, the USEPA promulgated NPDES permit application requirements for storm water discharges (40 CFR Parts 122, 123, and 124) which are applicable to FPUD Treatment Plant No. 1.  On April 17, 1997, the State Water Resources Control Board adopted Water Quality Order No. 97-03-DWQ, National Pollutant Discharge Elimination System (NPDES) General Permit No. CAS000001, Waste Discharge Requirements for Discharges of Storm Water Associated With Industrial Activities Excluding Construction Activities.  Storm water discharges from Treatment Plant No. 1 are subject to the terms and conditions of Water Quality Order No. 97-03-DWQ, as amended.

27.	On February 19, 1993, the USEPA issued the final rule for the use and disposal of sewage sludge (40 CFR Part 503).  This regulation requires that producers of sewage sludge meet certain reporting, handling, and disposal requirements.  USEPA, not this Regional Board, will oversee compliance with 40 CFR Part 503 (See Sludge Requirements, Section E.).

28.	Section 301(b)(1)(B) of the Clean Water Act (CWA) requires POTWs to meet effluent limitations based on secondary treatment as defined by the USEPA Administrator.  Secondary treatment is defined by the USEPA Administrator in the federal regulations (40 CFR Part 133.100 to 40 CFR Part 133.105) in terms of three parameters:  5-day biochemical oxygen demand (BOD5), total suspended solids (TSS), and pH.  Federal regulations allow substitution of 5-day carbonaceous biochemical oxygen demand (CBOD5) limitations for BOD5 limitations.  Order No. 89-13 substituted CBOD5 effluent limitations for the BOD5 effluent limitations.  Discharge Specification B.1.a. of this Order establishes effluent limitations for CBOD5, TSS, and pH in accordance with federal secondary treatment regulations.  In addition, Discharge Specification B.1.a of this Order establishes "Maximum at Any Time" limitations for CBOD5 and TSS based on best professional judgement.  In the absence of documentation that increased mass emission rate (MER) limitations are consistent with antidegradation policies, MER limitations in this Order must be the same as or more stringent than those in Order No. 95-08.  MER limitations for CBOD5 and TSS in this Order, therefore, are based on a flowrate of 1.95 MGallons/Day.  See Finding No. 30 of this Order.

29.	Waste discharge requirements for this discharge must be in conformance with 40 CFR 131.12 and State Board Resolution No. 68-16, Statement of Policy with Respect to Maintaining High Quality of Waters in California (known collectively as "antidegradation" policies).   The Regional Board has taken into consideration the requirements of the State and Federal “antidegradation” policies in establishing the requirements contained herein, and has determined that any reduction in water quality as a result of this discharge will not result in any long-term deleterious effects on water quality.  As the effluent concentration and mass emission rate limitations in this Order are the same as or more stringent than those in Order No. 95-08, except for differences due to rounding, significant figures, or calculation errors, adoption of this Order is consistent with antidegradation policies.

30.	Order No. 89-13 authorized an increase in flowrate from 1.95 MGallons/Day to 3.1 MGallons/Day.  In order to maintain consistency with antidegradation policies, mass emission rate (MER) limitations established by Order No. 89-13, and subsequently renewed in Order No. 95-08, were based on a flowrate of 1.95 MGallons/Day and were the same as or more stringent than those established in Order No. 83-19.  Similarly, MER limitations established by this Order are also based on a flowrate of 1.95 MGallons/Day and are the same as or more stringent than those established in Order No. 95-08.

31.	Effluent limitations, industrial pretreatment standards, sludge use and disposal regulations, and ocean discharge criteria established under Sections 208(b), 301, 302, 303(d), 304, 306, 307, 403, and 405 of the CWA, as amended (Title 33 United States Code (USC) 1251 et seq.), are applicable to the discharge(s) permitted by this Order.

32.	On May 9, 1996, this Regional Board adopted Order No. 96-04, General Waste Discharge Requirements Prohibiting Sanitary Sewer Overflows by Sewage Collection Agencies, and addenda thereto, to regulate sewage discharges from publicly owned sewage collection systems in the San Diego Region.  Order No. 96-04, serving as State Waste Discharge Requirements, prohibits the discharge of sewage from sanitary sewer systems at any point upstream of a sewage treatment plant.  Order No. 96-04 requires the development of a Sanitary Sewer Overflow Prevention Plan and a Sanitary Sewer Overflow Response Plan for each collection system in the Region.  In the event that a sewage discharge occurs within a collection system, Order No. 96-04 specifies procedures for reporting the discharge to the Regional Board.

33.	Monitoring and Reporting Program No. 2000-12 may be subject to changes during the 5 -year period of this permit.  The Southern California Coastal Water Research Project (SCCWRP) is currently investigating more effective techniques to monitor receiving waters of the Pacific Ocean.  Once the SCCWRP study is complete, these methods may be incorporated into this Order’s Monitoring and Reporting Program through an Addendum to this Order.

34.	The Regional Board, in establishing the requirements contained herein, considered factors including, but not limited to, the following:

- Beneficial uses to be protected and the water quality objectives

reasonably required for that purpose;

- Other waste discharges;

c.	The need to prevent nuisance;

d.	Past, present, and probable future beneficial uses of water;

e. 	Environmental characteristics of the receiving waters under consideration,

including the quality of those receiving waters;

- Water quality conditions that could reasonably be achieved through the coordinated control of all factors that affect water quality in the area;

g.	Economic considerations;

h.	The need for developing housing within the region; and

i.	The need to develop and use recycled water.

35.	The issuance of waste discharge requirements for this discharge is exempt from the requirement for preparation of environmental documents under the California Environmental Quality Act (Public Resources Code, Division 13, Chapter 3, Section 21000 et seq.) in accordance with the California Water Code, Section 13389.

36.	The Regional Board has notified the Fallbrook Public Utility District and all known interested parties of its intent to reissue the NPDES permit for the discharge from Treatment Plant No. 1 to the Pacific Ocean through the Oceanside Ocean Outfall via the Fallbrook Land Outfall.

37.	The Regional Board, in a public hearing on February 9, 2000, heard and considered all comments pertaining to the discharge from Fallbrook Public Utility District Treatment Plant No. 1 to the Pacific Ocean through the Oceanside Ocean Outfall via the Fallbrook Land Outfall.

38.	This Order shall serve as a National Pollutant Discharge Elimination System (NPDES) Permit for the discharge from the Fallbrook Public Utility District Treatment Plant No. 1 to the Pacific Ocean pursuant to Section 402 of the Clean Water Act, and amendments thereto.

IT IS HEREBY ORDERED that the Fallbrook Public Utility District (hereinafter discharger), in order to meet the provisions contained in Division 7 of the California Water Code and regulations adopted thereunder and the provisions of the Clean Water Act and the regulations adopted thereunder, shall comply with the following for the handling, treatment, and disposal of wastes through the Oceanside Ocean Outfall from Treatment Plant No. 1:

A.	PROHIBITIONS

1.	Discharges of wastes in a manner or to a location which have not been specifically authorized by this Order and for which valid waste discharge requirements are not in force are prohibited.

2.	The discharge of any radiological, chemical, or biological warfare agent, or high level radiological waste to the ocean is prohibited.

3.	The dumping or deposition, from shore or from vessels, of oil, garbage, trash or other solid municipal, industrial, or agricultural waste directly into waters subject to tidal action or adjacent to waters subject to tidal action in any manner which may permit it to be washed into waters subject to tidal action is prohibited.

4.	Waste shall not be discharged to areas designated as being of special biological significance.  Discharges shall be located a sufficient distance from such designated areas to assure maintenance of natural water quality conditions in these areas.

5.	Pipeline discharge of sludge to the ocean is prohibited by federal law; the discharge of municipal and industrial waste sludge directly to the ocean, or into a waste stream that discharges to the ocean, is prohibited.

6.	The discharge of sludge digester supernatant directly to the ocean, or into a waste stream that discharges to the ocean, without further treatment is prohibited.

7.	The bypassing of untreated wastes containing concentrations of pollutants in excess of those in Ocean Plan Table A or Table B or the effluent limitations of this Order to the ocean is prohibited, except as provided for in Provision F.36 of this Order.  (Also see Attachment No. 1 to this Order, 1997 Ocean Plan Discharge Prohibitions)

8.	Discharge through the Oceanside Ocean Outfall from any treatment facility at a 30-day average dry weather flowrate in excess of the secondary treatment design capacity of that treatment facility is prohibited.  For the purposes of this Order, the secondary treatment design capacity of a treatment facility is the existing secondary treatment design capacity of that treatment facility identified in the findings of this Order unless the discharger obtains the Executive Officer's approval of a revised design capacity in accordance with Provision F.17.

9.	Compliance with Discharge Prohibitions as stated in Chapter V of the 1997 Ocean Plan (Attachment No. 1) is required as a condition of this Order.

10.	Compliance with the Waste Discharge Prohibitions contained in the 1994 Basin Plan (Attachment No. 2) is required as a condition of this Order.

11.	Discharge to the Pacific Ocean from Fallbrook Public Utility District Wastewater Treatment Plant No. 1 via the Oceanside Ocean Outfall in excess of 2.7 MGallons/ Day is prohibited unless the discharger obtains revised waste discharge requirements authorizing an increased flowrate.

B.	DISCHARGE SPECIFICATIONS

1.	The following effluent limitations apply to the undiluted effluent discharged from Fallbrook Public Utility District Wastewater Treatment Plant No. 1 through the Oceanside Ocean Outfall.

a.	Effluent Limitations for Major Constituents and Properties of Wastewater

| Constituent/ Property | Units | Monthly Average (30 day) | Weekly Average (7 day) | Maximum at any time |
| --- | --- | --- | --- | --- |
| CBOD5,2 | mg/L lb/Day | 25 410 | 40 650 | 45 730 |
| total suspended solids1,2 | mg/L lb/Day | 30 490 | 45 730 | 50 810 |
| oil & grease | mg/L lb/Day | 25 410 | 40 650 | 75 1,200 |
| settleable solids2 | mL/L | 1.0 | 1.5 | 3.0 |
| turbidity2 | NTU | 75 | 100 | 225 |
| pH1,2 | pH units | Within limits of 6.0 - 9.0 at all times. |  |  |  |  |
| acute toxicity2 | TUa | 1.5 | 2.0 | 2.5 |

b.	Effluent Limitations on Toxic Materials for Protection of Marine Aquatic Life

| Constituent/ Property | Units | 6-Month Median | Daily Maximum | Instantaneous Maximum |
| --- | --- | --- | --- | --- |
| arsenic | mg/L lb/Day | 0.42 7.0 | 2.4 39 | 6.4 100 |
| cadmium | ug/L lb/Day | 83 1.4 | 330 5.4 | 830 13 |
| chromium (hexavalent) | ug/L lb/Day | 170 2.7 | 660 11 | 1,660 27 |
| copper | ug/L lb/Day | 85 1.4 | 830 14 | 2,300 38 |
| lead | ug/L lb/Day | 170 2.7 | 660 11 | 1,660 27 |
| mercury | ug/L lb/Day | 3.3 0.053 | 13 0.22 | 33 0.54 |
| nickel | mg/L lb/Day | 0.41 6.7 | 1.7 27 | 4.1 67 |
| selenium | mg/L lb/Day | 1.2 20 | 5.0 81 | 12 200 |
| silver | ug/L lb/Day | 24 0.39 | 140 2.2 | 360 5.9 |
| zinc | mg/L lb/Day | 1.0 16 | 6.0 97 | 16 260 |
| cyanide | ug/L lb/Day | 83 1.3 | 330 5.4 | 830 13 |
| total chlorine residual | ug/L lb/Day | 170 2.7 | 660 11 | 5,000 81 |
| ammonia (as N) | mg/L lb/Day | 50 810 | 200 3,200 | 500 8,100 |
| chronic toxicity | TUc | -- | 83 | -- |
| phenolic compounds (non-chlorinated) | mg/L lb/Day | 2.5 40 | 10 160 | 25 400 |
| chlorinated phenolics | ug/L lb/Day | 83 1.3 | 330 5.4 | 830 13 |
| endosulfan | ug/L lb/Day | 0.75 0.012 | 1.5 0.024 | 2.2 0.036 |
| endrin | ug/L lb/Day | 0.17 0.0027 | 0.33 0.0054 | 0.50 0.0081 |
| HCH | ug/L lb/Day | 0.33 0.0054 | 0.66 0.011 | 1.0 0.016 |
| radioactivity | Not to exceed limits specified in Title 17, Division 1, Chapter 5, Subsection 4, Group 3, Article 1, Section 30253 of the California Code of Regulations. |  |  |  |  |  |  |

c.	Effluent Limitations for Toxic, Non-carcinogenic Materials for Protection of Human Health3

| Constituent/ Property | Units | Monthly Average (30-day) |
| --- | --- | --- |
| acrolein | mg/L lb/Day | 18 300 |
| antimony | mg/L lb/Day | 100 1,600 |
| bis(2-chloroethoxy) methane | ug/L lb/Day | 360 5.9 |
| bis(2-chloroisopropyl) ether | mg/L lb/Day | 100 1,600 |
| chlorobenzene | mg/L lb/Day | 47 770 |
| chromium (III)4 | g/L lb/Day | 16 260,000 |
| di-n-butyl phthalate | mg/L lb/Day | 290 4,700 |
| Dichlorobenzenes | mg/L lb/Day | 420 6,900 |
| 1,1-dichloroethylene | mg/L lb/Day | 590 9,600 |
| diethyl phthalate | g/L lb/Day | 2.7 45,000 |
| dimethyl phthalate | g/L lb/Day | 68 1,100,000 |
| 4,6-dinitro-2-methylphenol | mg/L lb/Day | 18 300 |
| 2,4-dinitrophenol | ug/L lb/Day | 330 5.4 |
| ethylbenzene | mg/L lb/Day | 340 5,500 |
| fluoranthene | mg/L lb/Day | 1.2 20 |
| hexachlorocyclopentadiene | mg/L lb/Day | 4.8 78 |
| isophorone | g/L lb/Day | 12 200,000 |
| nitrobenzene | ug/L lb/Day | 410 6.6 |
| thallium | mg/L lb/Day | 1.2 19 |
| toluene | g/L lb/Day | 7.1 110,000 |
| 1,1,2,2-tetrachloroethane | mg/L lb/Day | 100 1,600 |
| tributyltin | ug/L lb/Day | 0.12 0.0019 |
| 1,1,1-trichloroethane | g/L lb/Day | 45 730,000 |
| 1,1,2-trichloroethane | g/L lb/Day | 3.6 58,000 |

d. 	Effluent Limitations for Toxic, Carcinogenic Materials for Protection of Human Health3

| Constituent/ Property | Units | Monthly Average (30-day) |
| --- | --- | --- |
| acrylonitrile | ug/L lb/Day | 8.3 0.13 |
| aldrin | ng/L lb/Day | 1.8 0.000030 |
| benzene | ug/L lb/Day | 490 8.0 |
| benzidine | ng/L lb/Day | 5.7 0.000093 |
| beryllium | ug/L lb/Day | 2.7 0.045 |
| bis(2-chloroethyl) ether | ug/L lb/Day | 3.7 0.061 |
| bis(2-ethylhexyl) phthalate | ug/L lb/Day | 290 4.7 |
| carbon tetrachloride | ug/L lb/Day | 75 1.2 |
| Chlordane | ng/L lb/Day | 1.9 0.000031 |
| chloroform | mg/L lb/Day | 11 180 |
| DDT | ug/L lb/Day | 0.014 0.00023 |
| 1,4-dichlorobenzene | mg/L lb/Day | 1.5 24 |
| 3,3-dichlorobenzidine | ug/L lb/Day | 0.67 0.011 |
| 1,2-dichloroethane | mg/L lb/Day | 11 180 |
| dichloromethane | mg/L lb/Day | 37 610 |
| 1,3-dichloropropene | ug/L lb/Day | 740 12 |
| dieldrin | ng/L lb/Day | 3.3 0.000054 |
| 2,4-dinitrotoluene | ug/L lb/Day | 220 3.5 |
| 1,2-diphenylhydrazine | ug/L lb/Day | 13 0.22 |
| Halomethanes | mg/L lb/Day | 11 180 |
| Heptachlor | ug/L lb/Day | 0.060 0.00097 |
| hexachlorobenzene | ug/L lb/Day | 0.017 0.00028 |
| hexachlorobutadiene | mg/L lb/Day | 1.2 19 |
| hexachloroethane | ug/L lb/Day | 210 3.4 |
| N-nitrosodimethylamine | ug/L lb/Day | 610 9.8 |
| N-nitrosodiphenylamine | ug/L lb/Day | 210 3.4 |
| PAHs | ug/L lb/Day | 0.73 0.012 |
| PCBs | ng/L lb/Day | 1.6 0.000026 |
| TCDD equivalents | pg/l lb/Day | 0.32 0.0000000053 |
| tetrachloroethylene | mg/L lb/Day | 8.2 130 |
| toxaphene | ug/L lb/Day | 0.017 0.00028 |
| trichloroethylene | mg/L lb/Day | 2.2 36 |
| 2,4,6-trichlorophenol | ug/L lb/Day | 24 0.39 |
| vinyl chloride | mg/L lb/Day | 3.0 49 |

mg/L = milligrams per liter

ug/L = micrograms per liter

ng/L = nanograms per liter

pg/L = picograms per liter

mL/L = milliliters per liter

NTU = Nephelometric Turbidity Units

TUa = toxic units acute

TUc = toxic units chronic

lb/Day = pounds per day

2.	Any significant change in waste flow shall be cause for reevaluating effluent quality requirements.

3.	The 30-day average percent removal of CBOD5 and the 30-day average percent removal of TSS shall each not be less than 85 percent.

4.	Waste management systems that discharge to the ocean must be designed and operated in a manner that will maintain the indigenous marine life and a healthy and diverse marine community.

5.	Waste discharged through the Oceanside Ocean Outfall must be essentially free of:

a.	Material that is floatable or will become floatable upon discharge.

b.	Settleable material or substances that form sediments which degrade benthic communities or other aquatic life.

c.	Substances which will accumulate to toxic levels in marine waters, sediments or biota.

d.	Substances that significantly decrease the natural light to benthic communities and other marine life.

e.	Materials that result in aesthetically undesirable discoloration of the ocean surface.

6.	Waste discharged through the Oceanside Ocean Outfall shall be discharged in a manner that provides sufficient initial dilution to minimize the concentrations of substances not removed in treatment.

7.	Location of waste discharges must be determined after a detailed assessment of the oceanographic characteristics and current patterns to assure that:

a.	Pathogenic organisms and viruses are not present in areas where shellfish are harvested for human consumption or in areas used for swimming or other body-contact sports.

b.	Natural water quality conditions are not altered in areas designated as being of special biological significance or areas that existing marine laboratories use as a source of seawater.

c.	Maximum protection is provided to the marine environment.

Waste that contains pathogenic organisms or viruses should be discharged a sufficient distance from shellfishing and water-contact sports areas to maintain applicable bacterial standards without disinfection.  Where conditions are such that an adequate distance cannot be attained, reliable disinfection in conjunction with a reasonable separation of the discharge point from the area of use must be provided.  Disinfection procedures that do not increase effluent toxicity and that constitute the least environmental and human hazard shall be used.

8.	All waste treatment, containment, and disposal facilities shall be protected against 100-year peak stream flows as defined by the San Diego County flood control agency.

9.	All waste treatment, containment, and disposal facilities shall be protected against erosion, overland runoff, and other impacts resulting from a 100-year frequency 24-hour storm.

10.	Collected screenings, sludges, and other solids removed from liquid wastes shall be disposed of in a manner approved by the Regional Board Executive Officer (hereinafter Executive Officer).

11.	The discharge of substances for which effluent limitations are not established by this Order shall be prevented or, if the discharge cannot be prevented, minimized.

C.	RECEIVING WATER LIMITATIONS

1.	The discharge of waste through the Oceanside Ocean Outfall shall not, by itself or jointly with any other discharge, cause violation of the following Ocean Plan ocean water quality objectives.  Compliance with the water quality objectives shall be determined from samples collected at stations representative of the area within the waste field where initial dilution is completed.

a.	Bacterial Characteristics

(1)	Water-Contact Standards

Within a zone bounded by the shoreline and a distance of 1,000 feet from the shoreline or the 30-foot depth contour, whichever is further from the shoreline, and in areas outside this zone used for water-contact sports, as determined by the Regional Board, but including all kelp beds, the following bacterial objectives shall be maintained throughout the water column:

(a)	Samples of water from each sampling station shall have a density of total coliform organisms less than 1,000 per 100 ml (10 per ml); provided that not more than 20 percent of the samples at any sampling station, in any 30-day period, may exceed 1,000 per 100 ml (10 per ml), and provided further that no single sample when verified by a repeat sample taken within 48 hours shall exceed 10,000 per 100 ml (100 per ml).

(b)	The fecal coliform density based on a minimum of not less than five samples for any 30-day period, shall not exceed a geometric mean of 200 per 100 ml nor shall more than 10 percent of the total samples during any 60-day period exceed 400 per 100 ml.

The "Initial Dilution Zone" of wastewater outfalls shall be excluded from designation as kelp beds for purposes of bacterial standards.  Adventitious assemblages of kelp plants on waste discharge structures (e.g., outfall pipes and diffusers) do not constitute kelp beds for purposes of bacterial standards.  Kelp beds, for the purpose of the bacterial standards of this Order, are significant aggregations of marine algae of the genera Macrocystis and Nereocystis.  Kelp beds include the total foliage canopy of Macrocystis and Nereocystis plants throughout the water column.

(2)	Shellfish Harvesting Standards

At all areas where shellfish may be harvested for human consumption, as determined by the Regional Board, the following bacterial objectives shall be maintained throughout the water column:

The median total coliform density shall not exceed 70 per 100 ml, and not more than 10 percent of the samples shall exceed 230 per 100 ml.

b.	Bacterial Assessment and Remedial Action Requirements

The requirements listed below shall be used to 1) determine the occurrence and extent of any impairment of a beneficial use due to bacterial contamination; 2) generate information which can be used in the development of an enterococcus standard; and 3) provide the basis for remedial actions necessary to minimize or eliminate any impairment of a beneficial use.

Measurement of enterococcus density shall be conducted at all stations where measurement of total and fecal coliforms are required.  In addition to the requirements of Receiving Water Limitation C.1.a of this Order, if a shore station consistently exceeds a coliform objective or exceeds a geometric mean enterococcus density of 24 organisms per 100 ml for a 30-day period or 12 organisms per 100 ml for a six-month period, the Regional Board shall require the discharger to conduct or participate in a survey to determine the source of the contamination.  The geometric mean shall be a moving average based on no less than five samples per month, spaced evenly over the time interval.  When a sanitary survey identifies a controllable source of indicator organisms associated with a discharge of sewage, the Regional Board may require the discharger and any other responsible parties identified by the Regional Board to take action to control the source.

c.	Physical Characteristics

(1)		Floating particulates and grease and oil shall not be visible.

(2)		The discharge of waste shall not cause aesthetically undesirable discoloration of the ocean surface.

(3)		Natural light shall not be significantly reduced at any point outside the initial dilution zone as a result of the discharge of waste.

(4)		The rate of deposition of inert solids and the characteristics of inert solids in ocean sediments shall not be changed such that benthic communities are degraded.

d.	Chemical Characteristics

(1)		The dissolved oxygen concentration shall not at any time be depressed more than 10 percent from that which occurs naturally, as a result of the discharge of oxygen-demanding waste materials.

(2)		The pH shall not be changed at any time more than 0.2 units from that which occurs naturally.

(3)		The dissolved sulfide concentration of waters in and near sediments shall not be significantly increased above that present under natural conditions.

(4)		The concentration of substances, set forth in Receiving Water Limitation C.3 of this Order, in marine sediments shall not be increased to levels which would degrade indigenous biota.

(5)		The concentration of organic materials in marine sediments shall not be increased to levels that would degrade marine life.

(6)		Nutrient materials shall not cause objectionable aquatic growths or degrade indigenous biota.

e.	Biological Characteristics

(1)		Marine communities, including vertebrate, invertebrate, and plant species, shall not be degraded.

(2)		The natural taste, odor, and color of fish, shellfish, or other marine resources used for human consumption shall not be altered.

(3)		The concentration of organic materials in fish, shellfish, or other marine resources used for human consumption shall not bioaccumulate to levels that are harmful to human health.

f.	Radioactivity

Discharge of radioactive waste shall not degrade marine life.

2.	The discharge of waste through the Oceanside Ocean Outfall shall not, by itself or jointly with any other discharge, cause violation of the following Basin Plan ocean water quality objectives:

a.	The mean annual dissolved oxygen concentration shall not be less than 7.0 mg/L nor shall the minimum dissolved oxygen concentration be reduced below 5.0 mg/L at any time.

b.	The pH value shall not be depressed below 7.0 nor raised above 8.6.

3.	Toxic Materials

The discharge through the Oceanside Ocean Outfall shall not by itself or jointly with any other discharge, cause the following Ocean Plan water quality objectives to be exceeded in the receiving water upon completion of initial dilution, except that limitations indicated for radioactivity shall apply directly to the undiluted waste effluent.

a.	Water Quality Objectives for the Protection of Marine Aquatic Life

| Constituent | Units | 6 Month Median | Daily Maximum | Instantaneous Maximum |
| --- | --- | --- | --- | --- |
| arsenic | ug/L | 8 | 32 | 80 |
| cadmium | ug/L | 1 | 4 | 10 |
| chromium (hexavalent) | ug/L | 2 | 8 | 20 |
| copper | ug/L | 3 | 12 | 30 |
| lead | ug/L | 2 | 8 | 20 |
| mercury | ug/L | 0.04 | 0.16 | 0.4 |
| nickel | ug/L | 5 | 20 | 50 |
| selenium | ug/L | 15 | 60 | 150 |
| silver | ug/L | 0.45 | 1.8 | 4.5 |
| zinc | ug/L | 20 | 80 | 200 |
| cyanide | ug/L | 1 | 4 | 10 |
| total chlorine residual | ug/L | 2 | 8 | 60 |
| ammonia (as N) | ug/L | 600 | 2,400 | 6,000 |
| chronic toxicity | TUc | -- | 1 | -- |
| phenolic compounds (non-chlorinated) | ug/L | 30 | 120 | 300 |
| chlorinated phenolics | ug/L | 1 | 4 | 10 |
| Endosulfan7 | ug/L | 0.009 | 0.018 | 0.027 |
| endrin | ug/L | 0.002 | 0.004 | 0.006 |
| HCH8 | ug/L | 0.004 | 0.008 | 0.012 |
| Radioactivity9 | Not to exceed limits specified in Title 17, Division 1, Chapter 5, Subsection 4, Group 3, Article 1, Section 30253 of the California Code of Regulations. |  |  |  |  |  |  |

b.	Water Quality Objectives for the Protection of Human Health -- Noncarcinogens

| Chemical | Units | 30-Day Average |
| --- | --- | --- |
| acrolein | ug/L | 220 |
| antimony | ug/L | 1,200 |
| bis(2-chloroethoxy)methane | ug/L | 4.4 |
| bis(2-chloroisopropyl)ether | ug/L | 1,200 |
| chlorobenzene | ug/L | 570 |
| chromium (III) | ug/L | 190,000 |
| di-n-butyl phthalate | ug/L | 3,500 |
| Dichlorobenzenes10 | ug/L | 5,100 |
| 1,1-dichloroethylene | ug/L | 7,100 |
| diethyl phthalate | ug/L | 33,000 |
| dimethyl phthalate | ug/L | 820,000 |
| 4,6-dinitro-2-methylphenol | ug/L | 220 |
| 2,4-dinitrophenol | ug/L | 4.0 |
| ethylbenzene | ug/L | 4,100 |
| fluoranthene | ug/L | 15 |
| hexachlorocyclopentadiene | ug/L | 58 |
| isophorone | ug/L | 150,000 |
| nitrobenzene | ug/L | 4.9 |
| thallium | ug/L | 14 |
| toluene | ug/L | 85,000 |
| 1,1,2,2-tetrachloroethane | ug/L | 1,200 |
| tributyltin | ug/L | 0.0014 |
| 1,1,1-trichloroethane | ug/L | 540,000 |
| 1,1,2-trichloroethane | ug/L | 43,000 |

c.	Water Quality Objectives for the Protection of Human Health -- Carcinogens

| Chemical | Units | 30-Day Average |
| --- | --- | --- |
| acrylonitrile | ug/L | 0.10 |
| aldrin | ug/L | 0.000022 |
| benzene | ug/L | 5.9 |
| benzidine | ug/L | 0.000069 |
| beryllium | ug/L | 0.033 |
| bis(2-chloroethyl)ether | ug/L | 0.045 |
| bis(2-ethylhexyl)phthalate | ug/L | 3.5 |
| carbon tetrachloride | ug/L | 0.90 |
| chlordane11 | ug/L | 0.000023 |
| chloroform | ug/L | 130 |
| DDT12 | ug/L | 0.00017 |
| 1,4-dichlorobenzene | ug/L | 18 |
| 3,3-dichlorobenzidine | ug/L | 0.0081 |
| 1,2-dichloroethane | ug/L | 130 |
| dichloromethane | ug/L | 450 |
| 1,3-dichloropropene | ug/L | 8.9 |
| dieldrin | ug/L | 0.00004 |
| 2,4-dinitrotoluene | ug/L | 2.6 |
| 1,2-diphenylhydrazine | ug/L | 0.16 |
| Halomethanes13 | ug/L | 130 |
| Heptachlor14 | ug/L | 0.00072 |
| hexachlorobenzene | ug/L | 0.00021 |
| hexachlorobutadiene | ug/L | 14 |
| hexachloroethane | ug/L | 2.5 |
| N-nitrosodimethylamine | ug/L | 7.3 |
| N-nitrosodiphenylamine | ug/L | 2.5 |
| PAHs15 | ug/L | 0.0088 |
| PCBs16 | ug/L | 0.000019 |
| TCDD equivalents17 | pg/L | 0.0039 |
| tetrachloroethylene | ug/L | 99 |
| toxaphene | ug/L | 0.00021 |
| trichloroethylene | ug/L | 27 |
| 2,4,6-trichlorophenol | ug/L | 0.29 |
| vinyl chloride | ug/L | 36 |

mg/L = milligrams per liter

ug/L = micrograms per liter

ng/l = nanograms per liter

pg/l = picograms per liter

NTU = Nephelometric Turbidity Unit

TUc = toxic units chronic

D.	PRETREATMENT REQUIREMENTS

1.	The discharger shall conduct an annual Industrial Waste Survey (IWS) of all the Industrial Users (IUs) in the service area of the Fallbrook Public Utility District (FPUD) in order to determine whether any such IUs are subject to pretreatment standards specified in 40 CFR 403.  The discharger shall also conduct an annual priority pollutant scan of the Wastewater Treatment Plant No. 1 effluent.  Based on the results of the IWS, the priority pollutant scan, and review of 40 CFR 403, the discharger shall submit an annual certification report indicating whether FPUD receives pollutants from any IU which would require the discharger to establish a pretreatment program in accordance with 40 CFR 403.  The annual certification reports, with the IWS and sampling results, shall be submitted no later than February 1st of each year.  If, and when, the discharger becomes aware of an IU in the service area of the FPUD which would require the FPUD to establish a pretreatment program pursuant to 40 CFR 403, the discharger shall notify the Regional Board requesting a modification of this Order and shall develop and implement a pretreatment program in accordance with the requirements of Sections 307(b) and (c), and 402(b)(8) of the CWA and 40 CFR 403.  The discharger shall assure that IUs in the service area of the FPUD subject to pretreatment standards promulgated in federal regulations or established by the discharger comply with those standards.

2.	The Regional Board may amend this Order, at any time, to require the discharger to develop and implement an industrial pretreatment program pursuant to the requirements of 40 CFR 403, if the Regional Board finds that the FPUD receives pollutants from an industry which is subject to pretreatment standards or if other circumstances warrant doing so.

3.	The FPUD provides for a program that protects the sewer system from disposal of toxic materials.  The program and activities implemented by the FPUD constitute the Nonindustrial Source Control Program.  To ensure continued protection of the sewer system, the FPUD shall review the sewer protection program that it implements and submit a written report at least once before the expiration date of this Order.

E.	SLUDGE REQUIREMENTS

1.	Management of all solids and sludge must comply with all requirements of CFR Parts 257, 258, 501, and 503, including all monitoring, record-keeping, and reporting requirements.  Since the State of California, hence the Regional and State Boards, has not been delegated the authority by the USEPA to implement the sludge program, enforcement of sludge requirements of CFR Part 503 is under USEPA's jurisdiction.

2.	All solids and sludge must be disposed of in a municipal solid waste landfill, reused by land application, or disposed of in a sludge-only landfill in accordance with 40 CFR Parts 503 and 258, and Title 23 CCR Chapter 15.  If the discharger desires to dispose of solids or sludge by a different method, a request for permit modification must be submitted to the USEPA and this Regional Board 180 days prior to the alternative disposal.

3.	Sludge that is disposed of in a municipal solid waste landfill must meet the requirements of 40 CFR 25.  In the annual self-monitoring report, the discharger shall include the amount of sludge disposed of, and the landfill(s) to which it was sent.

4.	The permittee shall ensure that all biosolids produced at its facility are used or disposed of in compliance with the applicable portions of:

a.	40 CFR 503: for biosolids which are land applied (placed on the land for the purpose of providing nutrients or conditioning the soil for crops or vegetation), placed in surface disposal sites (placed on the land for the purpose of disposal), stored, or incinerated;

b.	40 CFR 258: for biosolids disposed in a municipal solid waste landfill;

c.	40 CFR 257: for other disposal practices.

The permittee is responsible for ensuring compliance with these regulations whether the permittee uses or disposes of the biosolids itself or contracts with another party for further treatment, use, or disposal.  The permittee is responsible for informing subsequent preparers, appliers, and disposers of the requirements that they must meet under 40 CFR 257, 258, and 503.

5.	Notification of non-compliance: The permittee shall notify EPA Region 9, the San Diego Regional Board, and the Regional Board where the biosolids are used or disposed of any non-compliance within 24 hours if the non-compliance may seriously endanger health or the environment.  For other instances of non-compliance, the permittee shall notify EPA Region 9 and the Regional Boards of the non-compliance in writing within 5 working days of becoming aware of the non-compliance.  See Attachment No. 5 for Regional Board contact information.

6.	Inspection and Entry: The Regional Board, EPA, or an authorized representative, upon the presentation of credentials, shall be allowed by the permittee, directly or through contractual arrangements with the permittee’s biosolids contractors, a) to enter upon all premises where biosolids produced by the permittee are treated, stored, used, or disposed, b) to have access to and copy any records that must be kept under the conditions of this permit or of 40 CFR 503, and c) to inspect any facilities, equipment, or operations used by the permittee or its contractors in the production, treatment, storage, use, or disposal of the biosolids.

7.	The permittee shall submit an annual biosolids report to the EPA Region 9 Biosolids Coordinator and the Regional Board by February 19 of each year for the period covering the previous calendar year, with the following:

a.	The amount of biosolids generated that year, reported in dry metric tons, and the amount accumulated from previous years;

b.	The results of all pollutant and pathogen monitoring (Results shall be reported on a 100% dry weight basis for comparison with 40 CFR 503 limits.  Any sample results reported on a wet weight basis must report the % solids of that sample.);

c.	Descriptions of methods used to achieve pathogen reduction and vector attraction reduction, including supporting time and temperature data, and certifications required in 40 CFR 503.17 and 503.27;

d.	Names and addresses of entities receiving biosolids for further treatment, use, or disposal, and volumes of biosolids sent to each;

e.	For all biosolids used or disposed at the permittee's facilities, the site and management practice information and certification required in 40 CFR 503.17 and 503.27; and

f.	For all biosolids temporarily stored, the information required in 40 CFR 503.20 required to demonstrate temporary storage.

Reports shall be submitted to:

g.	(1)	Regional Biosolids Coordinator

USEPA (WTR-7)

75 Hawthorne St.

San Francisco, CA 94105-3901

(2)	Executive Officer

California Regional Water Quality Control Board

San Diego Region

9771 Clairemont Mesa Boulevard, Suite A

San Diego, California  92124-1324

Phone - (858) 467-2952

Fax - (858) 571-6972

8.	All the requirements of 40 CFR 503 and 23 CCR 15 are enforceable by the USEPA and this Regional Board whether or not the requirements are stated in an NPDES permit or any other permit issued to the discharger.

9.	The discharger shall take all reasonable steps to prevent and minimize any sludge use or disposal in violation of this Order that has a likelihood of adversely affecting human health or the environment.

10.	Solids and sludge treatment, storage, and disposal or reuse shall not create a nuisance, such as objectionable odors or flies, and shall not result in groundwater contamination.

11.	The solids and sludge treatment and storage site shall have facilities adequate to divert surface water runoff from adjacent areas, to protect the boundaries of the site from erosion, and to prevent drainage from the treatment and storage site.  Adequate protection is defined as protection from at least a 100-year storm and protection from the highest possible tidal stage that may occur.

12.	The discharge of sewage sludge and solids shall not cause waste material to be in a position where it is, or can be, conveyed from the treatment and storage sites and deposited in the waters of the state.

13.	The discharger shall submit an annual report to the USEPA and this Regional Board containing monitoring results and pathogen and vector attraction reduction requirements, as specified by 40 CFR 503.  The discharger shall also report the quantity of sludge disposed and the disposal method.  This self-monitoring report must be postmarked by February 1 of each year and report for the period covering the previous calendar year.

F.	PROVISIONS

1.	The discharger must comply with all conditions of this Order.  Any permit noncompliance constitutes a violation of the CWA and the California Water Code, and is grounds for enforcement action; for permit termination, revocation and reissuance, or modification; or for denial of an application for permit renewal, modification, or reissuance.

2.	The discharger must comply with all standard provisions, where applicable, as stated in 40 CFR 122.41 (see Attachment No. 3) and Standard Provisions (Attachment No. 4).

3.	Neither the treatment nor the discharge of waste shall create a pollution, contamination, or nuisance as defined by Section 13050 of the California Water Code.

4.	The following sections of 40 CFR (see Attachment No. 3) are incorporated into this permit by reference, and the discharger must comply with these provisions:

a.	122.5:	Effect of a permit

b.	122.21:	Application for a permit

c.	122.22:	Signatories to permit applications and reports

d.	122.41:	Conditions applicable to all permits

e.	122.61:	Transfer of permits

f.	122.62:	Modification or revocation of permits

g.	122.63:	Minor modifications of permits

h.	122.64:	Termination of permits

5.	This Order may be modified, revoked and reissued, or terminated for causes including, but not limited to, the following:

a.	Violation of any terms or conditions of this Order.

b.	Obtaining this Order by misrepresentation or failure to disclose fully all relevant facts.

c.	A change in any condition that requires either a temporary or permanent reduction or elimination of the authorized discharge.

The filing of a request by the discharger for modification, revocation and reissuance, or termination of this Order, or a notification of planned change in or anticipated noncompliance with this Order does not stay any condition of this Order.

6.	If any applicable toxic effluent standard or prohibition (including any schedule of compliance specified in such effluent standard or prohibition) is promulgated under Section 307(a) of the CWA for a toxic pollutant and that standard or prohibition is more stringent than any limitation on the pollutant in this Order, the Executive Officer may institute proceedings under these regulations to modify or revoke and reissue the Order to conform to the toxic effluent standard or prohibition.

7.	The discharger shall comply with effluent standards or prohibitions established under Section 307(a) of the CWA for toxic pollutants and with standards for sewage sludge use and disposal established under Section 405(d) of the CWA within the time provided in the regulations that establish those standards or prohibitions or standards for sewage sludge use or disposal, even if this Order has not yet been modified to incorporate the requirement.

8.	The discharger shall comply with all existing federal and state laws and regulations that apply to its sewage sludge use and disposal practice(s), and with the CWA Section 405(d) and 40 CFR Part 257.

9.	The discharger shall allow the Regional Board, or any Regional Board authorized representative, or any authorized representative of the USEPA (including an authorized contractor acting as a representative of the Regional Board or USEPA), upon the presentation of credentials and other documents as may be required by law, to:

a.	Enter upon the discharger's premises where a regulated facility or activity is located or conducted, including sludge use and disposal activities, or where records must be kept under the conditions of this Order;

b.	Have access to and copy, at reasonable times, any records that must be kept under the conditions of this Order;

c.	Inspect at reasonable times any facilities, equipment (including monitoring and control equipment), practices or operations regulated or required under this Order including sludge use and disposal sites; and

d.	Sample or monitor at reasonable times, for the purposes of assuring compliance with this Order or as otherwise authorized by the CWA or California Water Code, any substances or parameters at any location.

10.	This Order does not convey any property rights of any sort or any exclusive privilege.  The requirements prescribed herein do not authorize the commission of any act causing injury to persons or property, nor protect the discharger from its liabilities under federal, state, or local laws, nor create a vested right for the discharger to continue its waste discharge.

11.	It shall not be a defense for the discharger in an enforcement action that it would have been necessary to halt or reduce the permitted activity in order to maintain compliance with the conditions of this Order.  Upon reduction, loss, or failure of a treatment facility, the discharger shall, to the extent necessary to maintain compliance with this Order, control all discharges until the facility is restored or an alternative method of treatment is provided.  This provision applies, for example, when the primary source of power of a treatment facility fails, is reduced, or is lost.

12.	Supervisors and operators of the discharger's wastewater treatment facilities shall possess a certificate of appropriate grade in accordance with Chapter 14 of Division 4 of Title 23 of the California Code of Regulations.

13.	The discharger shall, at all times, properly operate and maintain all facilities and systems of treatment and control including sludge use and disposal facilities (and related appurtenances) which are installed or used by the discharger to achieve compliance with the conditions of this Order.  Proper operation and maintenance also includes adequate laboratory controls and appropriate quality assurance procedures.  This provision requires the operation of back-up or auxiliary facilities or similar systems which are installed by the discharger only when the operation is necessary to achieve compliance with the conditions of this Order.

14.	The discharger's wastewater treatment facilities shall be operated and maintained in accordance with the operation and maintenance manual(s) prepared by the discharger through the Clean Water Grant Program.

15.	A copy of this Order shall be posted at a prominent location at or near the treatment and disposal facilities, and shall be available to operating personnel at all times.

16.	The discharger shall comply with any interim effluent limitations as established by an addendum, enforcement action or revised waste discharge requirements which have been or may be adopted by this Regional Board.

17.	All proposed new treatment facilities and expansions of existing treatment facilities shall be completely constructed and operable prior to initiation of the discharge from the new or expanded facilities.  The discharger shall submit a certification report for each new treatment facility, expansion of an existing treatment facility, and re-rating of an existing treatment facility.  For new treatment facilities and expansions, the certification report shall be prepared by the design engineer.  For re-ratings, the certification report shall be prepared by the engineer who evaluated the treatment facility capacity.  The certification report shall:

a.	Identify the design capacity of the treatment facility;

b.	Certify the adequacy of each component of the treatment facility; and

c.	Contain a requirement-by-requirement analysis, based on acceptable engineering practices, of how the process and physical design of the facility will ensure compliance with this Order.

The signature and engineering license number of the engineer preparing the certification report shall be affixed to the report.  The certification report, should, if possible, be submitted prior to beginning construction.  The discharger shall not initiate a discharge from a new treatment facility or initiate a discharge from an existing treatment facility at a 30-day average dry weather flowrate in excess of its previously approved design capacity until:

d.	The certification report is received by the Executive Officer;

e.	The Executive Officer has received written notification of the completion of construction (new treatment facilities and expansions only);

f.	An inspection of the plant has been made by the Regional Board staff (new treatment facilities and expansions only); and

g.	The Executive Officer has provided the discharger with written authorization to discharge at a 30-day average dry weather flowrate not to exceed the revised design capacity.

18.	The discharger shall take all reasonable steps to minimize or prevent any discharge or sludge use or disposal in violation of this Order which has a reasonable likelihood of adversely affecting human health or the environment.

19.	If only one sample is collected during the time period associated with the effluent limitations (e.g., 30-day average or 6-month median), the single measurement shall be used to determine compliance with the effluent limitation for the entire time period.

20.	All analytical data shall be reported uncensored with detection limits and quantitation limits identified.  For any effluent limitation, compliance shall be determined using appropriate statistical methods to evaluate multiple samples.  Sufficient sampling and analysis shall be conducted to determine compliance.

21.	Compliance based on a single sample analysis shall be determined where appropriate as described below.

a.	When a calculated effluent limitation is greater than or equal to the PQL (defined below), compliance shall be determined based on the calculated effluent limitation and either single or multiple sample analyses.

b.	When the calculated effluent limitation is below the PQL, compliance determinations based on analysis of a single sample shall only be undertaken if the concentration of the constituent of concern in the sample is greater than or equal to the PQL.

c.	When the calculated effluent limitation is below the PQL and recurrent analytical responses between the PQL and the calculated limit occur, compliance shall be determined by statistical analysis of multiple samples.

22.	Published values for MDLs (defined below) and PQLs should be used except where revised MDLs and PQLs are available from recent laboratory performance evaluations, in which case the revised MDLs and PQLs should be used.  Where published values are not available, the Executive Officer will determine appropriate values based on available information, including information submitted by the discharger upon request of the Executive Officer.

a.	The Method Detection Limit (MDL) is the minimum concentration of a substance that can be measured and reported with 99% confidence that the analyte concentration is greater than zero, as defined in 40 CFR Part 136 Appendix B.

b.	The Practical Quantitation Level (PQL) is the lowest concentration of a substance which can be consistently determined within +/-20% of the true concentration by 75% of the labs tested in a performance evaluation study.  Alternatively, if performance data are not available, the PQL for carcinogens is the MDL x 5, and for noncarcinogens is the MDL x 10.

23.	When determining compliance based on a single sample, with a single effluent limitation which applies to a group of chemicals (e.g., PCBs), concentrations of individual members of the group may be considered to be zero if the analytical response for individual chemicals falls below the MDL for that parameter.

24.	The 6-month median effluent concentration limitation shall apply as a moving median of daily values for any 180-day period in which daily values represent flow-weighted average concentrations within a 24-hour period.  For intermittent discharges, the daily value shall be considered to equal zero for days on which no discharge occurred.  The 6-month median receiving water limitation shall apply as a moving median of all values collected for any 180-day period.

25.	The 30-day average effluent limitation shall be the moving arithmetic mean of daily concentrations over the specified 30-day period.

26.	The 7-day average shall be the moving arithmetic mean of daily concentrations over the specified 7-day period.

27.	The daily maximum effluent limitation shall apply to flow-weighted 24-hour composite samples.  The daily maximum receiving water limitation shall apply to grab sample determinations.

28.	The instantaneous maximum effluent limitation shall apply to grab sample determinations.  The instantaneous maximum receiving water limitation shall apply to grab sample determinations.

29.	The mass emission rate (MER), in pounds per day, shall be obtained from the following calculation for any calendar day:

mass emission rate (lb/Day) = 8.34 x Q x C

in which Q and C are the flow rate in MGallons/ Day and the constituent concentration in mg/L, respectively, and 8.34 is a conversion factor with units of [lb/MGallons] / [mg/L].  If a composite sample is taken, then C is the concentration measured in the composite sample and Q is the average flow rate occurring during the period over which the samples are composited.

30.	Compliance with the Acute Toxicity limitation in Discharge Specification B.1.a. of this Order shall be determined using an established protocol, e.g., American Society for Testing Materials (ASTM), USEPA, American Public Health Association, or State Board.  Acute Toxicity (TUa) shall be expressed in Toxic Units Acute (TUa), where:

TUa =       100

96-hour LC50

Where LC50 (Lethal Concentration 50%) is the percent waste giving 50% survival of test organisms.  LC50 shall be determined by static or continuous flow bioassay techniques using standard test species.  If specific identifiable substances in wastewater can be demonstrated by the discharger as being rapidly rendered harmless upon discharge to the marine environment, but not as a result of dilution, the LC50 may be determined after the test samples are adjusted to remove the influence of those substances.

When it is not possible to measure the 96-hour LC50 due to greater than 50% survival of the test species in 100% waste, the toxicity concentration shall be calculated by the following:

TUa = log (100 - S)

1.7

where S is the percentage survival in 100% waste.  If S > 99, TUa shall be reported as zero.

31.	Compliance with the Chronic Toxicity effluent limitation established in Discharge Specification No. B.1.b of this Order shall be determined using critical life stage toxicity tests.  Chronic Toxicity (TUc) shall be expressed as Toxic Units Chronic (TUc), where:

TUc =    100

NOEL

where NOEL is the No Observed Effect Level and is expressed as the maximum percent effluent that causes no observable effect on a test organism, as determined by the result of a critical life stage toxicity test listed below.

A minimum of three test species with approved test protocols shall be used to measure compliance with the chronic toxicity objective.  If possible, the test species shall include a fish, an invertebrate, and an aquatic plant.  After a screening period, monitoring may be reduced to the most sensitive species.  Dilution and control water should be obtained from an unaffected area of the receiving waters.  The sensitivity of the test organisms to a reference toxicant shall be determined concurrently with each bioassay test and reported with the test results.

The tests specified in the July 1997 Ocean Plan shall be used to measure TUc.  Other tests may be added to the list when approved by the SWRCB.

32.	If toxicity testing results show a violation of any acute or chronic toxicity limitation identified in Discharge Specification B.1 of this Order, the discharger shall:

a.	Take all reasonable measures necessary to immediately minimize toxicity; and

b.	Increase the frequency of the toxicity test(s) that showed a violation to at least two times per month until the results of at least two consecutive toxicity tests do not show violations.

If the Executive Officer determines that toxicity testing shows consistent violation of any acute or chronic toxicity limitation identified in Discharge Specification B.1. of this Order, the discharger shall conduct a Toxicity Reduction Evaluation (TRE) which includes all reasonable steps to identify the source of toxicity.  Once the source of toxicity is identified, the discharger shall take all reasonable steps to reduce the toxicity to meet the toxicity limitations identified in Discharge Specification B.1 of this Order.

Within fourteen days of completion of the TRE, the discharger shall submit the results of the TRE, including a summary of the findings, data generated, a list of corrective actions necessary to achieve consistent compliance with all the toxicity limitations of this Order and prevent recurrence of violations of those limitations, and a time schedule for implementation of such corrective actions.  The corrective actions and time schedule shall be modified at the direction of the Executive Officer.

33.	For all bacterial analyses, sample dilutions should be performed so the range of values extends from 2 to 16,000 MPN (most probable number).  The detection methods used for each analysis shall be reported with the results of the analysis.  Detection methods used for coliforms (total and fecal) shall be those presented in the most recent edition of Standard Methods for the Examination of Water and Wastewater or any improved method determined by the Regional Board (and approved by USEPA) to be appropriate.  Detection methods used for enterococcus shall be those presented in USEPA publication USEPA 600/4-85/076, Test Methods for Escherichia coli and Enterococci in Water By Membrane Filter Procedure or any improved method determined by the Regional Board to be appropriate.

34.	The geometric mean used for determining compliance with bacterial standards is calculated with the following equation:

Geometric Mean = (C1 x C2 x ... x Cn) 1/n

where n is the number of days samples were collected during the period and C is the concentration of bacteria (MPN/100 mL) found on each day of sampling.

35.	As used in this Order, waste includes a discharger's total discharge, of whatever origin (i.e. gross, not net, discharge).

36.	Bypass of Treatment Facilities

a.	Definitions

(1)	"Bypass" means the intentional diversion of waste streams from any portion of a treatment facility.

(2)	"Severe property damage" means substantial physical damage to property, damage to the treatment facilities which causes them to become inoperable, or substantial and permanent loss of natural resources which can reasonably be expected to occur in the absence of a bypass.  Severe property damage does not mean economic loss caused by delays in production.

b.	Bypass not Exceeding Limitations

The discharger may allow any bypass to occur which does not cause effluent limitations of this Order or the concentrations of pollutants set forth in Ocean Plan Table A or Table B to be exceeded, but only if it also is for essential maintenance to assure efficient operation.  These bypasses are not subject to the provisions of paragraphs c. and d. of this provision.

c.	Notice

(1)	Anticipated bypass.  If the discharger knows in advance of the need for a bypass, it shall submit prior notice, if possible, at least ten days before the date of the bypass.

(2)	Unanticipated bypass.  The discharger shall submit notice of an unanticipated bypass as required in Reporting Requirement G.11 of this Order.

d.	Prohibition of Bypass

(1)	Bypass is prohibited and the Regional Board may take enforcement action against the discharger for bypass, unless:

(a)	Bypass was unavoidable to prevent loss of life, personal injury, or severe property damage;

(b)	There were no feasible alternatives to the bypass, such as the use of auxiliary treatment facilities, retention of untreated wastes, or maintenance during normal periods of equipment downtime.  This condition is not satisfied if adequate back-up equipment should have been installed in the exercise of reasonable engineering judgment to prevent a bypass which occurred during normal periods of equipment downtime or preventive maintenance; and

(c)	The discharger submitted notices as required under paragraph c. of this provision.

(2)	The Executive Officer may approve an anticipated bypass, after considering its adverse effect, if the Executive Officer determines that it will meet the three conditions listed in paragraph d.(1) of this provision.

37.	Upset

a.	Definition

"Upset" means an exceptional incident in which there is unintentional and temporary noncompliance with technology based permit effluent limitations because of factors beyond the reasonable control of the discharger.  An upset does not include noncompliance to the extent caused by operational error, improperly designed treatment facilities, inadequate treatment facilities, lack of preventive maintenance, or careless or improper operation.

b.	Effect of an Upset

An upset constitutes an affirmative defense to an action brought for noncompliance with such technology-based permit effluent limitations if the requirements of paragraph c. of this provision are met.  No determination made during administrative review of claims that noncompliance was caused by upset, and before an action for noncompliance, is final administrative action subject to judicial review.

c.	Conditions Necessary for a Demonstration of Upset

A discharger who wishes to establish the affirmative defense of upset shall demonstrate, through properly signed, contemporaneous operating logs, or other relevant evidence that:

(1)	An upset occurred and that the discharger can identify the cause(s) of the upset;

(2)	The permitted facility was at the time being properly operated;

(3)	The discharger submitted notice of the upset as required in Reporting Requirement G.11 of this Order; and

(4)	The discharger complied with any remedial measures required under Provision F.18 of this Order.

d.	Burden of Proof

In any enforcement proceeding the discharger seeking to establish the occurrence of an upset has the burden of proof.

38.	The discharger shall maintain a Sewer Overflow Prevention Plan (SOPP) in an up-to-date condition and shall amend the SOPP whenever there is a change (e.g. in the design, construction, operation, or maintenance of the sewerage system or sewerage facilities) which materially affects the potential for sewer overflows.  The discharger shall review and amend the SOPP as appropriate after each sewer overflow from the Fallbrook Land Outfall (FLO) or in the service area of Wastewater Treatment Plant No. 1.  The SOPP and any amendments thereto, shall be subject to the approval of the Executive Officer and shall be modified as directed by the Executive Officer.  The discharger shall submit the SOPP and any amendments thereto to the Executive Officer upon request of the Executive Officer.  The discharger shall ensure that the up-to-date SOPP is readily available to sewerage system personnel at all times and that sewerage system personnel are familiar with it.

39.	The discharger shall maintain a Sewer Overflow Response Plan (SORP) for the FLO and the service area of Wastewater Treatment Plant No. 1.  The SORP shall establish procedures for responding to sewer overflows from the FLO and in the service area of Wastewater Treatment Plant No. 1 so as to (a) minimize the sewer overflow volume which enters surface waters, and (b) minimize the adverse effects of sewer overflows on water quality and beneficial uses.  The discharger shall maintain the SORP in an up-to-date condition and shall amend the SORP as necessary to accomplish these objectives.  The discharger shall review and amend the SORP as appropriate after each sewer overflow from the FLO and in the service area of Wastewater Treatment Plant No. 1.  The SORP, and any amendments thereto, shall be subject to the approval of the Executive Officer and shall be modified as directed by the Executive Officer.  The discharger shall submit the SORP and any amendments thereto to the Executive Officer upon request of the Executive Officer.  The discharger shall ensure that the up-to-date SORP is readily available to sewerage system personnel at all times and that sewerage system personnel are familiar with it.

G.	REPORTING REQUIREMENTS

1.	The discharger must comply with standard monitoring and reporting requirements, where applicable, as stated in 40 CFR 122.41 (see Attachment No. 3) and Standard Provisions (Attachment No. 4).

- This Order expires February 9, 2005.  If the discharger wishes to continue an activity regulated by this Order after the expiration date of this Order, the discharger must apply for and obtain new waste discharge requirements.  The discharger must submit a full and complete Report of Waste Discharge in accordance with Title 23 of the California Code of Regulations, to the Executive Officer, not later than 180 days in advance of the expiration date of this Order, as application for issuance of new waste discharge requirements.  Not less than 180 days prior to any material change in the character, location, volume, or amount of waste discharge, the Discharger shall submit a technical report describing such changes.  Such changes include but are not limited to the following:

- Addition of a major industrial waste discharge to a discharge of essentially domestic sewage, or the addition of a new process or product by an industrial facility resulting in a change in the character of the waste;

- Significant change in disposal method (e.g., change from land disposal to a direct discharge to water, or change in the method of treatment which would significantly alter the characteristics of the waste);

- Significant change in the disposal area (e.g., moving the discharge to another drainage area, to a different water body, or to a disposal area significantly removed from the original area potentially causing different water quality or nuisance problems);

- Increase in flow beyond that specified in the waste discharge requirements;

- Increase in area or depth to be used for solid waste disposal beyond that specified in the waste discharge requirements [CWC 13372, 13376, 13264, 23 CCR 2210];

- Any substantial change in the amount or characteristics of pollutants used, handled, stored, or generated;

- Any new discharge of pollutants or new potential pollutant source; and/or

- Other circumstances which could result in a material change in the character, amount, or location of discharges. [CWC 13372, 13264,23 CCR 2210]

3.	All applications, reports, or information submitted to the Executive Officer of this Regional Board shall be signed and certified.

a.	All Reports of Waste Discharge shall be signed by either a principal executive officer or ranking elected official.

b.	All reports required by this Order and other information requested by the Executive Officer shall be signed by a person described in paragraph a. of this reporting requirement, or by a duly authorized representative of that person.  A person is a duly authorized representative only if:

(1)	The authorization is made in writing by a person described in paragraph a. of this reporting requirement;

(2)	The authorization specifies either an individual or a position having responsibility for the overall operation of the regulated facility or activity such as the position of plant manager, operator of a well or a well field, superintendent, position of equivalent responsibility, or an individual or position having overall responsibility for environmental matters for the company (A duly authorized representative may thus be either a named individual or any individual occupying a named position.); and

(3)	The written authorization is submitted to the Executive Officer.

c.	If an authorization under paragraph b. of this reporting requirement is no longer accurate because a different individual or position has responsibility for the overall operation of the facility, a new authorization satisfying the requirements of paragraph b. of this reporting requirement must be submitted to the Executive Officer prior to or together with any reports, information, or applications to be signed by an authorized representative.

d.	Any person signing a document under paragraph a. or b. of this reporting requirement shall make the following certification:

"I certify under penalty of law that this document and all attachments were prepared under my direction or supervision in accordance with a system designed to assure that qualified personnel properly gather and evaluate the information submitted.  Based on my inquiry of the person or persons who manage the system, or those persons directly responsible for gathering the information, the information submitted is, to the best of my knowledge and belief, true, accurate, and complete.  I am aware that there are significant penalties for submitting false information, including the possibility of fine and imprisonment for knowing violations."

4.	Pursuant to State Board Order No. WQ 84-7, the discharger shall submit with its Report of Waste Discharge for reissuance of its NPDES permit, sufficient information to justify why any effluent proposed to be discharged to the ocean is not being reclaimed for beneficial use.

5.	The discharger shall report sewer overflow events in accordance with the following procedures:

a.	A sewer overflow event is a discharge of treated or untreated wastewater at a location not authorized by waste discharge requirements and/or a NPDES permit, which results from a pump station failure, sewer line break, obstruction, surcharge, or any other operational dysfunction.  Overflows that occur within the treatment plant facility shall be reported to the Regional Board, the Office of Emergency Services (OES), and the County of San Diego Department of Environmental Health Services, following the procedures listed below.  All sewer overflows within the collection system service area of the treatment facility shall be reported as specified in this Regional Board’s Order No. 96-04, General Waste Discharge Requirements Prohibiting Sanitary Sewer Overflows by Sewage Collection Agencies.  The sewage overflow reporting requirements in this order coincide with the reporting requirements contained in Order No. 96-04.

b.	For the purpose of this permit, discharges to storm drains are considered discharges to surface waters.

c.	The following are the reporting procedures for sewage overflows from sewage treatment and disposal facilities:

(1)	If a sanitary sewer overflow event results in a discharge that is greater than 1,000 gallons or that reaches surface waters, the discharger shall:

(a)	Report the sanitary sewer overflow event to the Regional Board, OES, and the County of San Diego Environmental Health Services by telephone, by voice mail, or by FAX within 24 hours from the time the discharger becomes aware of the sewer overflow event.  This report shall include only the information specified by Item Nos. 1 through 5, 8, 12A, 12B, and 13 contained in the Sewer Overflow Report (SOR) form supplied by the Regional Board.

(b)	A SOR form, as well as any additional pertinent information, shall be submitted to the Regional Board no later than five days following the starting date of the sewer overflow event.

(c)	The discharge event shall be included in the next quarterly self-monitoring report, in accordance with the format described in Order No. 96-04.

(2)	If the sanitary sewer overflow event results in a discharge under 1,000 gallons or the discharge does not reach surface waters:

(a)	A report is not required within 24 hours.

(b)	The discharge event shall be included in the next quarterly self-monitoring report, in accordance with the format described in Order No. 96-04.

6.	The discharger shall provide adequate notice to the Executive Officer of the following:

a.	Any new introduction of pollutants into the discharger's treatment works from an indirect discharger which would be subject to Section 301 or 306 of the CWA if it were directly discharging those pollutants;

b.	Any substantial change in the volume or character of pollutants being introduced into the discharger's treatment works by a source introducing pollutants into the treatment works at the time of issuance of this Order; and

c.	For purposes of this paragraph, adequate notice shall include information on:

(1)	The quality and quantity of effluent introduced into the POTW, and

(2)	Any anticipated impact of the change on the quantity or quality of effluent and/or sludge to be discharged from the POTW.

7.	The discharger shall give notice to the Executive Officer as soon as possible of any planned physical alterations or additions to the permitted facility.  Notice is required only when:

a.	The alteration or addition to a permitted facility may meet one of the criteria for determining whether a facility is a new source in 40 CFR Part 122.29(b);

b.	The alteration or addition could significantly change the nature or increase the quantity of pollutants discharged.  This notification applies to pollutants which are not subject to effluent limitations in this Order; or

c.	The alteration or addition results in a significant change in the discharger's sludge use or disposal practices, and such alteration, addition, or change may justify the application of conditions in this Order that are different from or absent in the existing Order, including notification of additional use or disposal sites not reported during the permit application process or not reported pursuant to an approved land application plan.

8.	The discharger shall give advance notice to the Executive Officer of any planned changes in the permitted facility or activity which may result in noncompliance with the requirements of this Order.

9.	This Order is not transferable to any person except after notice to the Executive Officer.  The Executive Officer may require modification or revocation and reissuance of this Order to change the name of the discharger and incorporate such other requirements as may be necessary under the CWA or the California Water Code in accordance with the following:

a.	Transfers by Modification

Except as provided in paragraph b. of this reporting requirement, this Order may be transferred by the discharger to a new owner or operator only if this Order has been modified or revoked and reissued, or a minor modification made to identify the new discharger and incorporate such other requirements as may be necessary under the CWA or California Water Code.

b.	Automatic Transfers

As an alternative to transfers under paragraph a. of this reporting requirement, any NPDES permit may be automatically transferred to a new discharger if:

(1)	The current discharger notifies the Executive Officer at least 30 days in advance of the proposed transfer date in paragraph b.(2) of this reporting requirement;

(2)	The notice includes a written agreement between the existing and new dischargers containing a specific date for transfer of permit responsibility, coverage, and liability between them; and

(3)	The Executive Officer does not notify the existing discharger and the proposed new discharger of his or her intent to modify or revoke and reissue the permit.  A modification under this subparagraph may also be a minor modification under 40 CFR Part 122.63.  If this notice is not received, the transfer is effective on the date specified in the agreement mentioned in paragraph b.(2) of this reporting requirement.

10.	The discharger shall conduct monitoring and submit reports in accordance with Monitoring and Reporting Program (MRP) No. 2000-12.  Monitoring results shall be reported at the intervals specified in MRP No. 2000-12.

11.	The discharger shall report any noncompliance which may endanger human health or the environment.  Any information shall be provided orally to the Executive Officer within 24 hours from the time the discharger becomes aware of the circumstances.  A written submission shall also be provided within 5 days of the time the discharger becomes aware of the circumstances.  A written submission shall contain a description of the noncompliance and its cause; the period of noncompliance, including exact dates and times, and if the noncompliance has not been corrected, the anticipated time it is expected to continue; and steps taken or planned to reduce, eliminate, and prevent recurrence of the noncompliance.  The Executive Officer, or an authorized representative may waive the written report on a case-by-case basis if the oral report has been received within 24 hours.  The following shall be included as information which must be reported within 24 hours under this reporting requirement:

a.	Any unanticipated bypass which exceeds any effluent limitation in this Order;

b.	Any upset which exceeds any effluent limitation in this Order;

c.	Violation of a daily maximum effluent limitation as specified in this Order for the following pollutants:

(1)	Chronic Toxicity

(2)	Arsenic

(3)	Cadmium

(4)	Chromium (Hexavalent)

(5)	Copper

(6)	Lead

(7)	Mercury

(8)	Nickel

(9)	Selenium

(10)	Silver

(11)	Zinc

(12)	Cyanide

(13)	Total Chlorine Residual

(14)	Ammonia

(15)	Phenolic Compounds (non-chlorinated)

(16)	Chlorinated Phenolics

(17)	Endosulfan

(18)	Endrin

(19)	HCH

d.	Any violation of effluent limitations for acute toxicity as specified in this Order;

e.	Any violation of the prohibitions of this Order; and

f.	Any finding of levels of bacteria in a receiving water sample which exceeds bacterial water quality objectives specified in Receiving Water Limitation C.1.a.(1) of this Order.

12.	The discharger shall furnish to the Executive Officer, SWRCB Executive Director, or USEPA, within a reasonable time, any information which the Executive Officer, SWRCB Executive Director, or USEPA may request to determine whether cause exists for modifying, revoking and reissuing, or terminating this Order, or to determine compliance with this Order.  The discharger shall also furnish to the Executive Officer, SWRCB Executive Director, or USEPA, upon request, copies of records required to be kept by this Order.

13.	The discharger shall report all instances of noncompliance not reported under Reporting Requirements G.10, G.11, and G.16 of this Order, at the time monitoring reports are submitted.  The reports shall contain the information listed in Reporting Requirement  G.11 of this Order.

14.	Where the discharger becomes aware that it failed to submit any relevant facts in a Report of Waste Discharge, or submitted incorrect information in a Report of Waste Discharge, or in any report to the Regional Board, it shall promptly submit such facts or information.

15.	Whenever a receiving water sample is found to contain levels of bacteria which exceed bacterial water quality objectives specified in Receiving Water Limitation C.1.a. (1) of this Order, the discharger shall immediately notify the County of San Diego Department of Environmental Health Services and post signs prohibiting body contact with the water in all areas affected by the contamination.

16.	Reports of compliance or noncompliance with, or any progress reports on, interim and final requirements contained in any compliance schedule of this permit shall be submitted no later than 14 days following each schedule date.

17.	The discharger shall submit a written report to the Executive Officer within 90 days after the average dry weather influent flowrate for any 30-day period equals or exceeds 75 percent of the design capacity of the waste treatment and/or disposal facilities.  The discharger's senior administrative officer shall sign a letter which transmits that report and certifies that the policy-making body is adequately informed about it.  The report shall include:

a.	Average daily flow for the 30-day period, the date on which the instantaneous peak flow occurred, the rate of that peak flow, and the total flow for that day;

b.	The discharger's best estimate of when the average daily dry-weather flowrate will equal or exceed the design capacity of the facilities; and

c.	The discharger's intended schedule for studies, design, and other steps needed to provide additional capacity for the waste treatment and/or disposal facilities, and/or to control the flowrate before the waste flowrate equals the capacity of the POTW’s present unit operations and processes.

18.	Except for data determined to be confidential under 40 CFR Part 2, all reports prepared in accordance with the terms of this Order shall be available for public inspection at the offices of the California Regional Water Quality Control Board, San Diego Region.  As required by the CWA, Reports of Waste Discharge, this Order, and effluent data shall not be considered confidential.

19.	The discharger shall submit reports and provide notifications to the Regional Board and other agencies as specified in this Order.  These other agencies include USEPA and the San Diego County Department of Health Services.  Reports shall be submitted and notifications shall be made to:

a.		Executive Officer

California Regional Water Quality Control Board

San Diego Region

9771 Clairemont Mesa Boulevard, Suite A

San Diego, California  92124-1324

Phone - (858) 467-2952

Fax - (858) 571-6972

b.	Regional Administrator

U.S. Environmental Protection Agency

Region 9

75 Hawthorne Street

San Francisco, California  94105

c.	Department of Environmental Health

County of San Diego

P.O. Box 129261

San Diego, California  92112-9261

Phone - (619) 338-2222  [Monday – Friday, 7:30 AM to 4:30 PM]

After Hours - (858) 565-5255  [County Communications Dispatch, request dispatcher to page the Hazardous Materials Specialist]

Fax - (619) 338-2848

d.	Office of Emergency Services (OES)

Phone - (916) 262-1621 or 1- (800) 852-7550

Fax - (916) 262-1677

H.	NOTIFICATIONS

1.	California Water Code Section 13263(g) states:

No discharge of waste into the waters of the state, whether or not such discharge is made pursuant to waste discharge requirements, shall create a vested right to continue such discharge.  All discharges of waste into waters of the state are privileges, not rights.

2.	The discharger is held accountable for responsibilities, liabilities, legal actions, and penalties as stated in Attachment No. 3 and Attachment No. 4 of this Order.

3.	This Order shall become effective 10 days after the date of its adoption provided the Regional Administrator, USEPA, has no objection.  If the Regional Administrator objects to its issuance, this Order shall not become effective until such objection is withdrawn.

4.	This Order supersedes Order No. 95-08 when this Order becomes effective.

I, John H. Robertus, Executive Officer of the San Diego Regional Water Quality Control Board, do hereby certify the foregoing is a full, true, and correct copy of Order No. 2000-12 adopted by the California Regional Water Quality Control Board, San Diego Region, on February 9, 2000.

______________________________

JOHN H. ROBERTUS

Executive Officer

ORDER NO. 2000-12 ENDNOTES

Secondary treatment is defined by the USEPA Administrator in the federal regulations (40 CFR Part 133.100 to 40 CFR Part 133.105) in terms of three parameters: 5-day biochemical oxygen demand (BOD5), total suspended solids (TSS), and pH.  Federal regulations allow substitution of 5-day carbonaceous biochemical oxygen demand (CBOD5) limitations for BOD5 limitations.  See also Finding No. 28 of this Order.

Effluent concentration limitations are specified in the 1997 Ocean Plan, Table A.  For consistency with antidegradation policies, mass emission rate (MER) limitations, where applicable, were determined using procedures outlined in the 1997 Ocean Plan, Equation 2, and a flowrate of 1.95 MGallons/ Day, as described in Finding Nos. 29 and 30 of this Order.

Effluent limitations were determined using the procedures outlined in the 1997 Ocean Plan, and an initial dilution of 82.  Mass emission rate (MER) limitations were determined using procedures outlined in the 1997 Ocean Plan, Equation 2, and a flowrate of 1.95 MGallons/ Day.

The discharger may, at its option, meet this limitation as a total chromium limitation.

If the discharger can demonstrate to the satisfaction of the Regional Board (subject to EPA approval) that an analytical method is available to reliably distinguish between strongly and weakly complexed cyanide, effluent limitations for cyanide may be met by the combined measurement of free cyanide, simple alkali metal cyanides, and weakly complexed organometallic cyanide complexes.  In order for the analytical method to be acceptable, the recovery of free cyanide from metal complexes must be comparable to that achieved by Standard Methods 412 F, G, and H (Standard Methods for the Examination of Water and Wastewater, Joint Editorial Board, American Public Health Association, American Water Works Association, and Water Pollution Control Federation, most recent edition).

The effluent concentration and mass emission rate limitations for total chlorine residual are based on a continuous discharge of chlorine.  Effluent concentration limitations for total chlorine residual, which are applicable to intermittent discharges not exceeding 2 hours, shall be determined through the use of the following equations:

log Co = -0.43 (log x) + 1.8

Ce = Co + Dm (Co - Cs)

where:

Co	=  the concentration (in ug/L) to be met at the completion of initial dilution

x	=  the duration of uninterrupted chlorine discharge in minutes

Ce	=  the effluent concentration limitation (in ug/L) to apply when chlorine is being intermittently discharged

Dm	=  the minimum probable initial dilution

Cs	=  the background seawater concentration = 0

Endosulfan shall mean the sum of endosulfan-alpha and -beta and endosulfan sulfate.

HCH shall mean the sum of the alpha, beta, gamma (lindane) and delta isomers of hexachlorocyclohexane.

The 1997 Ocean Plan refers to limits specified in Title 17, Division 5, Chapter 4, Group 3, Article 3, Section 32069 of the California Code of Regulations.  The referenced section has since been repealed and the limitations set forth in this Order will be substituted.  According to SWRCB staff, the change will be reflected in subsequent Ocean Plan revisions.

Dichlorobenzenes shall mean the sum of 1,2- and 1,3-dichlorobenzene.

Chlordane shall mean the sum of chlordane-alpha, chlordane-gamma, chlordene-alpha, chlordene-gamma, nonachlor-alpha, nonachlor-gamma, and oxychlordane.

DDT shall mean the sum of 4,4'DDT, 2,4'DDT, 4,4'DDE, 2,4'DDE, 4,4'DDD, and 2,4'DDD.

Halomethanes shall mean the sum of bromoform, bromomethane (methyl bromide), chloromethane (methyl chloride), chlorodibromomethane, and dichlorobromomethane.

Heptachlor shall mean the sum of heptachlor and heptachlor epoxide.

PAHs (polynuclear aromatic hydrocarbons) shall mean the sum of acenaphthylene, anthracene, 1,2-benzanthracene, 3,4-benzofluoranthene, benzo[k]fluoranthene, 1,12-benzoperylene, benzo[a]pyrene, chrysene, dibenzo[ah]anthracene, fluorene, indeno[1,2,3-cd]pyrene, phenanthrene and pyrene.

PCBs (polychlorinated biphenyls) shall mean the sum of chlorinated biphenyls whose analytical characteristics resemble those of Aroclor-1016, Aroclor-1221, Aroclor-1232, Aroclor-1242, Aroclor-1248, Aroclor-1254 and Aroclor-1260.

TCDD EQUIVALENTS shall mean the sum of the concentrations of chlorinated dibenzodioxins (2,3,7,8-CDDs) and chlorinated dibenzofurans (2,3,7,8-CDFs) multiplied by their respective toxicity factors, as shown in the table below.

Isomer Group			Toxicity Equivalence Factor

2,3,7,8-tetra CDD				1.0

2,3,7,8-penta CDD			0.5

2,3,7,8-hexa CDDs			0.1

2,3,7,8-hepta CDD			0.01

octa CDD				0.001

2,3,7,8 tetra CDF				0.1

1,2,3,7,8 penta CDF			0.05

2,3,4,7,8 penta CDF			0.5

2,3,7,8 hexa CDFs			0.1

2,3,7,8 hepta CDFs			0.01

octa CDF				0.001