CALIFORNIA REGIONAL WATER QUALITY CONTROL BOARD

SAN DIEGO REGION

ORDER NO. 99-71

NPDES NO. CA0107999

WASTE DISCHARGE REQUIREMENTS

FOR THE

SAN ELIJO JOINT POWERS AUTHORITY

SAN ELIJO WATER RECLAMATION FACILITY

DISCHARGE TO THE PACIFIC OCEAN

VIA THE SAN ELIJO OCEAN OUTFALL

Table of Contents

Findings									2

- Prohibitions									9

- Discharge Specifications							11

- Receiving Water Limitations						19

- Pretreatment Requirements						26

- Sludge Requirements							27

- Provisions									28

- Reporting Requirements							35

- Notifications									39

- Order No. 99-71 Endnotes							40

- Attachment 1 (Ocean Plan Discharge Prohibitions)			42

- Attachment 2 (Basin Plan Discharge Specifications)			43

- Attachment 3 (Standard Provisions from 40 CFR 122.41-42)		46

- Attachment 4 (Region 9 Standard Provisions)				61

- Attachment 5 (Standard Provisions 40 CFR by Reference)		66

- Monitoring and Reporting Program No. 99-71				104

- Purpose									104

- Monitoring Provisions							104

- Influent Monitoring							107

- Effluent Monitoring							107

- Solids Monitoring							110

- Receiving Water Monitoring						110

- Monitoring and Reporting Program Endnotes			117

CALIFORNIA REGIONAL WATER QUALITY CONTROL BOARD

SAN DIEGO REGION

ORDER NO. 99-71

NPDES NO. CA0107999

WASTE DISCHARGE REQUIREMENTS

FOR THE

SAN ELIJO JOINT POWERS AUTHORITY

SAN ELIJO WATER POLLUTION CONTROL FACILITY

DISCHARGE TO THE PACIFIC OCEAN

VIA THE SAN ELIJO OCEAN OUTFALL

The California Regional Water Quality Control Board, San Diego Region (hereinafter referred to as Regional Board) finds that:

1. 	On July, 1, 1981, this Regional Board adopted Order No. 81-12, National Pollutant Discharge Elimination System (NPDES) Permit No. CA0107999, Waste Discharge Requirements for the San Elijo Water Pollution Control Facility, San Diego County.  Order No. 81-12, and Addenda Nos. 1 and 2 thereto, established requirements for the discharge of up to 3.7 million gallons per day (MGallons/ Day) of treated wastewater from the San Elijo Water Pollution Control Facility (SEWPCF) to the Pacific Ocean via the San Elijo Ocean Outfall.  Order No. 81-12 had an expiration date of June 1, 1986.

2.	On June 6, 1988, this Regional Board adopted Order No. 88-21, NPDES No. CA0107999,  Waste Discharge Requirements for the San Elijo Water Pollution Control Facility Discharge Through the San Elijo Ocean Outfall, San Diego County, which superseded Order No. 81-12.  Order No. 88-21, and Addenda Nos. 1 and 2 thereto, established requirements for the discharge of an average dry weather flow rate of 3.7 MGallons/Day of treated wastewater from the SEWPCF to the Pacific Ocean via the San Elijo Ocean Outfall.  Order No. 88-21, as amended, had an expiration date of June 6, 1993. Monitoring and Reporting Program No. 81-12, as modified by Technical Change Order Nos. T-1 and T-2 remained in effect with the adoption of Order No. 88-21, as no new monitoring and reporting program was issued with Order No. 88-21.

3.	On December 9, 1992, the San Elijo Joint Powers Authority (SEJPA) submitted an application for renewal of its NPDES permit, pursuant to Reporting Requirement No. E.11 of Order No. 88-21, and requested an increase in authorized flow rate from 3.7 MGallons/ Day to the discharger’s upgraded design flow of 5.25 MGallons/ Day.

4.	On June 26, 1993, the SEJPA notified the Regional Board that it had completed construction of and startup operations for the secondary treatment facilities at the SEWPCF.

5.	On November 10, 1994, this Regional Board established Order No. 94-105, which contains requirements for the discharge of an average dry weather flow rate of 3.7 MGallons/ Day of treated wastewater from the SEWPCF to the Pacific Ocean via the San Elijo Ocean Outfall, superseding Order No. 88-21.  Order No. 94-105 did not authorize an increase in flow rate from 3.7 MGallons/ Day to 5.25 MGallons/ Day.  On July 1, 1995 Technical Change Order No.1 substituted Monitoring and Reporting Program 94-105 in its entirety.

6.	The SEWPCF, now called the San Elijo Water Reclamation Facility (SEWRF) is a publicly owned treatment works (POTW) owned by the SEJPA which treats residential and commercial wastewater generated in the City of Solana Beach, Rancho Santa Fe Community Services District (RSFCSD), and the Cardiff Sanitation District.  The SEJPA is a joint powers authority established to provide treatment and disposal of wastewater.  The City of Solana Beach, RSFCSD, and the Cardiff Sanitation District are the member agencies that comprise the SEJPA.  The SEJPA currently contracts with the consulting firm of Camp Dresser & McKee Inc. as its authorized agent for the operation and administration of the SEWRF.

7.	The SEWRF is located in the Cardiff area of the City of Encinitas, on 2695 Manchester Avenue, in a small canyon on approximately 27 acres immediately west of Interstate Highway 5 on the north side of San Elijo Lagoon.

8.	Wastewater treatment unit operations and processes at the SEWRF consist of preliminary treatment by screening and aerated grit removal, primary sedimentation using clarifiers, and biological treatment using activated sludge followed by secondary clarification.  Sludge is anaerobically digested and mechanically dewatered using belt filter presses.  Final sludge disposal is by offsite reuse and/or disposal in a landfill. The SEJPA is completing construction of tertiary treatment facilities at the SEWRF to reclaim wastewater for beneficial use.  Tertiary treatment will include coagulation and flocculation, filtration, and UV-disinfection.  Once complete, the discharge of reclaimed water for beneficial use will be regulated by Order No. 93-71, Waste Discharge Requirements for the San Elijo Joint Powers Authority San Elijo Water Pollution Control Facility, San Diego County.

9.	Since the 1993 upgrade to secondary treatment, the design capacity at the SEWRF has been changed to 5.25 MGallons/ Day.  The NPDES permitted capacity has remained 3.7 MGallons/ Day.  Monitoring reports indicate that the average dry weather flowrate is currently approximately 3.5 MGallons/ Day.

10.	On May 10, 1999 the SEJPA submitted an application for renewal of its NPDES permit, requesting a permitted discharge of 5.25 MGallons/ Day at the SEWRF.  On July 13, 1999 SEJPA re-submitted their application with a few modifications, and after minor revisions on August 11, 1999, the permit application was determined to be complete.

11.	Effluent from the SEWRF is discharged to the Pacific Ocean through the San Elijo Ocean Outfall (SEOO).  The SEOO is owned by the SEJPA, and currently 79% of the SEOO capacity is leased to the City of Escondido.  A separate NPDES permit (CA0107981) regulates the discharge through the SEOO from the City of Escondido.

12.	The SEOO extends southwesterly from a point approximately 2,200 feet south of the mouth of San Elijo Lagoon.  The inshore end of the diffuser is located approximately 6,800 feet offshore at a depth of approximately 110 feet.  The diffuser, which is collinear with the outfall, is approximately 1,200 feet long and extends to a depth of approximately 148 feet.  The terminus of the diffuser is located at Latitude 33 00' 21" North, Longitude 117 18' 9" West.

13.	The design capacity of the SEOO is 25.5 MGallons/ Day.  The current operating capacity of the SEOO is approximately 24.3 MGallons/ Day.  The addition of 1.55 MGallons/Day to the SEWRF’s previously permitted 3.7, in combination with the City of Escondido’s permitted 16.5 MGallons/Day results in a net discharge of 21.75 MGallons/Day to the SEOO.  Based on characteristics of the SEOO, State Water Resources Control Board (SWRCB) staff has determined the minimum initial dilution for the SEOO, with 200 diffuser ports open and a flowrate of 24 MGallons/ Day, to be 220, using the computer model UMERGE.

14.	The SWRCB adopted a revised Water Quality Control Plan for Ocean Waters of California (California Ocean Plan) on July 23, 1997.  The Ocean Plan identifies the following beneficial uses of state ocean waters to be protected:

a.	Industrial water supply

b.	Navigation

c.	Water contact recreation

- Non-contact water recreation

- Ocean commercial and sport fishing

- Preservation and enhancement of Areas of Special Biological Significance

g.	Preservation of rare and endangered species

h.	Marine habitat

- Mariculture

- Fish migration

k.	Fish spawning

- Shellfish harvesting

m.	Aesthetic enjoyment

In order to protect these beneficial uses, the Ocean Plan establishes water quality objectives (for bacterial, physical, chemical, and biological characteristics, and for radioactivity), general requirements for management of waste discharge to the ocean, quality requirements for waste discharges (effluent water quality requirements), discharge prohibitions, and general provisions.

15.	The Comprehensive Water Quality Control Plan Report, San Diego Basin (9), (Basin Plan) was adopted by this Regional Board on March 17, 1975 and subsequently approved by the SWRCB. Subsequent revisions to the Basin Plan have also been adopted by the Regional Board and approved by the SWRCB.

16.	The Basin Plan identifies the following beneficial uses of state ocean waters to be protected:

a.	Industrial service supply

b.	Navigation

c.	Water contact recreation

d.	Noncontact water recreation

e.	Ocean commercial and sport fishing

f.	Preservation of Areas of Special Biological Significance (ASBS)

g.	Preservation of rare and endangered species

h.	Marine habitat

i.	Mariculture

j.	Fish migration

k.	Fish spawning

l.	Shellfish harvesting

m.	Wildlife habitat

The Basin Plan relies primarily on the requirements of the Ocean Plan for protection of these beneficial uses.  However, the Basin Plan establishes additional water quality objectives for dissolved oxygen and pH.

- The 1997 Ocean Plan states that, “Water shall not be discharged to areas designated as being of special biological significance.  Discharges shall be located a sufficient distance from such designated areas to assure maintenance of natural water quality conditions in that area.”

The marine habitat beneficial use identified in both the Ocean Plan and Basin Plan provides for the preservation of the marine ecosystem in the City of Encinitas Marine Life Refuge.  The City of Encinitas Marine Life Refuge, described in Fish and Game Code Section 10913, is located approximately 11,000 feet northeast of the inshore end of the SEOO diffuser.  The refuge is generally bounded to the north by the westerly prolongation of the northerly right-of-way line of D Street, and to the south by the southwesterly prolongation of the southeasterly line of Lot N in Block 3 of Resubdivision of Sea Cliff Villa in the City of Encinitas, and includes submerged lands and ocean waters 600 feet west of the mean high tide line.

Regional Board staff’s review of the monitoring data submitted by the discharger in accordance with the Monitoring and Reporting Program of Order No. 94-105 have not revealed any impacts on the City of Encinitas Marine Life Refuge resulting from the SEOO discharge.  No impacts to the refuge area are expected to occur in the future.

18.	Receiving Water Limitation No. C.1a. (2) of this Order establishes bacterial objectives for areas where shellfish may be harvested for human consumption, as determined by the Regional Board.  However, as of the date of adoption of this Order, this Regional Board has not designated any shellfish harvesting area.  If and when this Regional Board, in consultation with the Department of Fish and Game, health agencies, and other interested parties, does designate shellfish harvesting areas in the vicinity of this discharge, this Order will be amended to identify the area(s) to which Receiving Water Limitation No. C.1a. (2) applies.

19.	Federal regulations (40 CFR Part 403) establish pretreatment program requirements for POTWs that receive pollutants from industries subject to pretreatment standards. Since the SEWRF does not currently receive pollutants from any industry subject to federal pretreatment standards, the SEJPA is not required to have an industrial pretreatment program at this time.  However, this Order requires the SEJPA to conduct a semiannual survey to determine if the SEWRF receives pollutants from any industry subject to pretreatment standards and to submit a semiannual certification report based on that survey.  (See Pretreatment Requirements, Section D.)  The Regional Board may amend this Order, at any time, to require the discharger to develop and implement an industrial pretreatment program pursuant to the requirements of 40 CFR Part 403, if the Regional Board finds that the SEWRF receives pollutants from an industry which is subject to pretreatment standards or if other circumstances warrant doing so.

20.	On November 16, 1990, the United States Environmental Protection Agency (USEPA) promulgated NPDES permit application requirements for storm water discharges (40 CFR Parts 122, 123, and 124) which are applicable to the SEWRF.  On November 19, 1991, the State Water Resources Control Board adopted Water Quality Order No. 91-13-DWQ, National Pollutant Discharge Elimination System (NPDES) General Permit No. CAS000001, Waste Discharge Requirements for Discharges of Storm Water Associated with Industrial Activities Excluding Construction Activities.  Storm water discharges from the SEWRF are subject to the terms and conditions of Water Quality Order No. 91-13-DWQ, as amended.

- Municipal storm water discharges are regulated separately under NPDES Order No. 90-42 (CA0108758), Waste Discharge Requirements for Storm Water and Urban Runoff from the County of San Diego, the Incorporated Cities of San Diego County, and the San Diego Unified Port District.  The SEJPA is considered a co-permittee participant in this permit.

- On February 19, 1993, the USEPA issued the final rule for the use and disposal of sewage sludge (40 CFR Part 503).  This regulation requires that producers of sewage sludge meet certain reporting, handling, and disposal requirements.  USEPA, not this Regional Board, will oversee compliance with 40 CFR Part 503.

- Section 301(b)(1)(B) of the Clean Water Act (CWA) requires POTWs to meet effluent limitations based on secondary treatment as defined by the USEPA Administrator.  Secondary treatment is defined by the USEPA Administrator in the federal regulations (40 CFR Part 133.100 to 40 CFR Part 133.105) in terms of three parameters: 5-day biochemical oxygen demand (BOD5), total suspended solids (TSS), and pH.  Federal regulations allow substitution of 5-day carbonaceous biochemical oxygen demand (CBOD5) limitations for BOD5 limitations.  By letter dated June 4, 1993, the SEJPA requested that CBOD5 limitations be incorporated in the SEWRF permit renewal in lieu of BOD5 requirements.  Following the approval of this Regional Board, Order No. 94-105 was modified to establish limits for CBOD5 , replacing BOD5 limitations.  This permit continues to reflect that change.  Discharge Specification B.1.a. of this Order establishes effluent limitations for CBOD5, TSS, and pH in accordance with federal secondary treatment regulations.  In addition, Discharge Specification B.1.a of this Order establishes  "Maximum at Any Time" limitations for CBOD5 and TSS.  Mass emission rate (MER) limitations have been calculated using a flow rate of 5.25 MGallons/ Day.

24.	Effluent limitations, industrial pretreatment standards, sludge use and disposal regulations, and ocean discharge criteria established under Sections 208(b), 301, 302, 303(d), 304, 306, 307, 403, and 405 of the CWA, as amended (Title 33 United States Code (USC) 1251 et seq.), are applicable to the discharge.

25.	Waste discharge requirements for this discharge must be in conformance with 40 CFR 131.12 and State Board Resolution No. 68-16, Statement of Policy with Respect to Maintaining High Quality of Waters in California (known collectively as "antidegradation" policies).   The Regional Board has taken into consideration the requirements of the State and Federal “antidegradation” policies in establishing the requirements contained herein, and has determined that any reduction in water quality as a result of this discharge will not result in any long-term deleterious effects on water quality.

26.	Monitoring and Reporting Program No. 99-71 may be subject to changes during the 5 -year period of this permit.  The Southern California Coastal Water Research Project (SCCWRP) is currently investigating more effective techniques to monitor receiving waters of the Pacific Ocean.  Once the SCCWRP study is complete, these methods may be incorporated into this Order’s Monitoring and Reporting Program through an Addendum to this Order.

27.	The Regional Board, in establishing the requirements contained herein, considered factors including, but not limited to, the following:

- Beneficial uses to be protected and the water quality objectives

reasonably required for that purpose;

- Other waste discharges;

c.	The need to prevent nuisance;

d.	Past, present, and probable future beneficial uses of water;

e. 	Environmental characteristics of the receiving waters under consideration,

including the quality of those receiving waters;

- Water quality conditions that could reasonably be achieved through the coordinated control of all factors that affect water quality in the area;

g.	Economic considerations;

h.	The need for developing housing within the region; and

i.	The need to develop and use recycled water.

28.	The issuance of waste discharge requirements for this discharge is exempt from the requirement for preparation of environmental documents under the California Environmental Quality Act (Public Resources Code, Division 13, Chapter 3, Section 21000 et seq.) in accordance with the California Water Code, Section 13389.

29.	The Regional Board has notified the San Elijo Joint Powers Authority and all known interested parties of its intent to reissue the NPDES permit for the discharge from the San Elijo Water Reclamation Facility to the Pacific Ocean.

30.	The Regional Board, in a public hearing on November 10, 1999, has heard and considered all comments pertaining to the discharge from the San Elijo Water Reclamation Facility to the Pacific Ocean via the San Elijo Ocean Outfall.

31.	This Order shall serve as a NPDES Permit for the discharge from the San Elijo Joint Powers Authority San Elijo Water Reclamation Facility to the Pacific Ocean pursuant to Section 402 of the Clean Water Act, and amendments thereto.

IT IS HEREBY ORDERED that the San Elijo Joint Powers Authority (hereinafter discharger), in order to meet the provisions contained in Division 7 of the California Water Code and regulations adopted thereunder and the provisions of the Clean Water Act and the regulations adopted thereunder, shall comply with the following for the handling, treatment, and disposal of wastes through the San Elijo Ocean Outfall from the San Elijo Joint Powers Authority San Elijo Water Reclamation Facility:

A.	PROHIBITIONS

1.	Discharges of wastes in a manner or to a location which have not been specifically authorized by this Order and for which valid waste discharge requirements are not in force are prohibited.

2.	The dumping or deposition, from shore or from vessels, of oil, garbage, trash or other solid municipal, industrial, or agricultural waste directly into waters subject to tidal action or adjacent to waters subject to tidal action in any manner which may permit it to be washed into waters subject to tidal action is prohibited.

3.	Compliance with Discharge Prohibitions as stated in Chapter V of the 1997 Ocean Plan (Attachment 1) is required as a condition of this Order.

- Compliance with the Waste Discharge Prohibitions contained in the 1994 Basin Plan (Attachment 2) is also required as a condition of this Order.

- Discharge to the Pacific Ocean from the San Elijo Water Reclamation Facility via the San Elijo Ocean Outfall in excess of 5.25 MGallons/ Day is prohibited unless the discharger obtains revised waste discharge requirements authorizing an increased flowrate.

B.	DISCHARGE SPECIFICATIONS

1.	The following effluent limitations apply to the undiluted effluent discharged from the San Elijo Water Reclamation Facility through the San Elijo Ocean Outfall.

a.	Effluent Limitations for Major Constituents and Properties of Wastewater

| Constituent/ Property | Units | Monthly Average (30 day) | Weekly Average (7 day) | Maximum at any time |
| --- | --- | --- | --- | --- |
| CBOD5 | mg/L lb/Day | 25 1,100 | 40 1,800 | 45 2,000 |
| total suspended solids1,2 | mg/L lb/Day | 30 1,300 | 45 2,000 | 50 2,200 |
| oil & grease | mg/L lb/Day | 25 1,100 | 40 1,800 | 75 3,300 |
| settleable solids2 | mL/L | 1.0 | 1.5 | 3.0 |
| turbidity2 | NTU | 75 | 100 | 225 |
| PH1,2 | pH units | Within limits of 6.0 - 9.0 at all times. |  |  |  |  |
| acute toxicity2 | TUa | 1.5 | 2.0 | 2.5 |

b.	Effluent Limitations on Toxic Materials for Protection of Marine Aquatic Life

| Constituent/ Property | Units | 6-Month Median | Daily Maximum | Instantaneous Maximum |
| --- | --- | --- | --- | --- |
| arsenic | ug/L lb/Day | 1,100 49 | 6,400 280 | 17,000 750 |
| cadmium | ug/L lb/Day | 220 9.7 | 880 39 | 2,200 97 |
| chromium (hexavalent) | ug/L lb/Day | 440 19 | 1,800 77 | 4,400 190 |
| copper | ug/L lb/Day | 220 9.8 | 2,200 97 | 6,200 270 |
| lead | ug/L lb/Day | 440 19 | 1,800 77 | 4,400 190 |
| mercury | ug/L lb/Day | 8.7 0 .38 | 35 1.5 | 88 3.9 |
| nickel | ug/L lb/Day | 1,100 48 | 4,400 190 | 11,000 480 |
| selenium | ug/L lb/Day | 3,300 145 | 13,000 580 | 33,000 1,500 |
| silver | ug/L lb/Day | 64 2.8 | 360 16 | 960 42 |
| zinc | ug/L lb/Day | 2,700 120 | 16,000 700 | 42,000 1,900 |
| cyanide | mg/L lb/Day | 0.22 9.7 | 0.88 39 | 2.2 97 |
| total chlorine residual | mg/L lb/Day | 0.44 19 | 1.8 77 | 13 580 |
| ammonia (as N) | mg/L lb/Day | 130 5,800 | 530 23,000 | 1,300 58,000 |
| chronic toxicity | TUc | -- | 200 | -- |
| phenolic compounds (non-chlorinated) | mg/L lb/Day | 6.6 290 | 27 1,200 | 66 2,900 |
| Constituent/ Property | Units | 6-Month Median | Daily Maximum | Instantaneous Maximum |
| chlorinated phenolics | mg/L lb/Day | 0.22 9.7 | 0.88 39 | 2.2 97 |
| endosulfan | ug/L lb/Day | 2.0 0.087 | 4.0 0.17 | 6.0 0.26 |
| endrin | ug/L lb/Day | 0.44 0.019 | 0.88 0.039 | 1.3 0.058 |
| HCH | ug/L lb/Day | 0.88 0.039 | 1.8 0.077 | 2.7 0.12 |
| radioactivity | Not to exceed limits specified in Title 17, Division 1, Chapter 5, Subsection 4, Group 3, Article 1, Section 30253 of the California Code of Regulations. |  |  |  |  |  |  |

c.	Effluent Limitations for Toxic, Non-carcinogenic Materials for Protection of Human Health3

| Constituent/ Property | Units | Monthly Average (30-day) |
| --- | --- | --- |
| acrolein | ug/L lb/Day | 49,000 2,100 |
| antimony | ug/L lb/Day | 270,000 12,000 |
| bis(2-chloroethoxy) methane | ug/L lb/Day | 970 43 |
| bis(2-chloroisopropyl) ether | ug/L lb/Day | 270,000 12,000 |
| chlorobenzene | ug/L lb/Day | 130,000 5,500 |
| chromium (III)4 | ug/L lb/Day | 42,000,000 1,800,000 |
| di-n-butyl phthalate | ug/L lb/Day | 770,000 34,000 |
| Dichlorobenzenes | ug/L lb/Day | 1,100,000 49,000 |
| 1,1-dichloroethylene | ug/L lb/Day | 1,600,000 69,000 |
| diethyl phthalate | ug/L lb/Day | 7,300,000 320,000 |
| dimethyl phthalate | ug/L lb/Day | 180,000,000 7,900,000 |
| 4,6-dinitro-2-methylphenol | ug/L lb/Day | 49,000 2,100 |
| 2,4-dinitrophenol | ug/L lb/Day | 880 38 |
| ethylbenzene | ug/L lb/Day | 910,000 40,000 |

| Constituent/ Property | Units | Monthly Average (30-day) |
| --- | --- | --- |
| fluoranthene | ug/L lb/Day | 3,300 150 |
| hexachlorocyclopentadiene | ug/L lb/Day | 13,000 560 |
| isophorone | ug/L lb/Day | 33,000,000 1,500,000 |
| nitrobenzene | ug/L lb/Day | 1,100 47 |
| thallium | ug/L lb/Day | 3,100 140 |
| toluene | ug/L lb/Day | 19,000,000 820,000 |
| 1,1,2,2-tetrachloroethane | ug/L lb/Day | 270,000 12,000 |
| tributyltin | ug/L lb/Day | 0.31 0.014 |
| 1,1,1-trichloroethane | ug/L lb/Day | 120,000,000 5,200,000 |
| 1,1,2-trichloroethane | ug/L lb/Day | 9,500,000 420,000 |

d. Effluent Limitations for Toxic, Carcinogenic Materials for Protection of Human Health3

| Constituent/ Property | Units | Monthly Average (30-day) |
| --- | --- | --- |
| acrylonitrile | ug/L lb/Day | 22 0.97 |
| aldrin | ug/L lb/Day | 0.0049 0.00021 |
| benzene | ug/L lb/Day | 1,300 57 |
| benzidine | ug/L lb/Day | 0.015 0.00067 |
| beryllium | ug/L lb/Day | 7.3 0.32 |
| bis(2-chloroethyl)ether | ug/L lb/Day | 10 0.44 |
| bis(2-ethylhexyl)phthalate | ug/L lb/Day | 770 34 |
| carbon tetrachloride | ug/L lb/Day | 200 8.7 |
| Chlordane | ug/L lb/Day | 0.0051 0.00022 |
| chloroform | ug/L lb/Day | 29,000 1,300 |
| DDT | ug/L lb/Day | 0.038 0.0017 |
| 1,4-dichlorobenzene | ug/L lb/Day | 4,000 170 |
| 3,3-dichlorobenzidine | ug/L lb/Day | 1.8 0.078 |
| 1,2-dichloroethane | ug/L lb/Day | 29,000 1,300 |
| dichloromethane | ug/L lb/Day | 99,000 4,400 |

| Constituent/ Property | Units | Monthly Average (30-day) |
| --- | --- | --- |
| 1,3-dichloropropene | ug/L lb/Day | 2,000 86 |
| dieldrin | ug/L lb/Day | 0.0088 0.00039 |
| 2,4-dinitrotoluene | ug/L lb/Day | 570 25 |
| 1,2-diphenylhydrazine | ug/L lb/Day | 35 1.5 |
| Halomethanes | ug/L lb/Day | 29,000 1,300 |
| Heptachlor | ug/L lb/Day | 0.16 0.0070 |
| hexachlorobenzene | ug/L lb/Day | 0.046 0.002 |
| hexachlorobutadiene | ug/L lb/Day | 3,100 140 |
| hexachloroethane | ug/L lb/Day | 550 24 |
| N-nitrosodimethylamine | ug/L lb/Day | 1,600 71 |
| N-nitrosodiphenylamine | ug/L lb/Day | 550 24 |
| PAHs | ug/L lb/Day | 1.9 0.085 |
| PCBs | ug/L lb/Day | 0.0042 0.00018 |
| TCDD equivalents | pg/l lb/Day | 0.86 0.000000038 |
| tetrachloroethylene | ug/L lb/Day | 22,000 960 |
| toxaphene | ug/L lb/Day | 0.046 0.002 |

| Constituent/ Property | Units | Monthly Average (30-day) |
| --- | --- | --- |
| trichloroethylene | ug/L lb/Day | 6,000 260 |
| 2,4,6-trichlorophenol | ug/L lb/Day | 64 2.8 |
| vinyl chloride | ug/L lb/Day | 8,000 350 |

mg/L = milligrams per liter

ug/L = micrograms per liter

ng/L = nanograms per liter

pg/L = picograms per liter

mL/L = milliliters per liter

NTU = Nephelometric Turbidity Units

TUa = toxic units acute

TUc = toxic units chronic

lb/Day = pounds per day

2.	Any significant change in waste flow shall be cause for reevaluating effluent quality requirements.

3.	The 30-day average percent removal of CBOD5 and TSS shall not be less than 85 percent.

4.	Waste management systems that discharge to the ocean must be designed and operated in a manner that will maintain the indigenous marine life and a healthy and diverse marine community.

5.	Waste discharged through the San Elijo Ocean Outfall must be essentially free of:

a.	Material that is floatable or will become floatable upon discharge.

b.	Settleable material or substances that form sediments which degrade benthic communities or other aquatic life.

c.	Substances which will accumulate to toxic levels in marine waters, sediments or biota.

d.	Substances that significantly decrease the natural light to benthic communities and other marine life.

e.	Materials that result in aesthetically undesirable discoloration of the ocean surface.

6.	Waste discharged through the San Elijo Ocean Outfall shall be discharged in a manner that provides sufficient initial dilution to minimize the concentrations of substances not removed in treatment.

7.	Waste that contains pathogenic organisms or viruses should be discharged a sufficient distance from shellfishing and water-contact sports areas to maintain applicable bacterial standards without disinfection.  Where conditions are such that an adequate distance cannot be attained, reliable disinfection in conjunction with a reasonable separation of the discharge point from the area of use must be provided.  Disinfection procedures that do not increase effluent toxicity and that constitute the least environmental and human hazard shall be used.

8.	All waste treatment, containment and disposal facilities shall be protected against 100-year peak stream flows as defined by the San Diego County flood control agency.

9.	All waste treatment, containment and disposal facilities shall be protected against erosion, overland runoff and other impacts resulting from a 100-year frequency 24-hour storm.

10.	Collected screenings, sludges, and other solids removed from liquid wastes shall be disposed of in a manner approved by the Regional Board Executive Officer (hereinafter Executive Officer).

11.	The discharge of substances for which effluent limitations are not established by this Order shall be prevented or, if the discharge cannot be prevented, minimized.

C.	RECEIVING WATER LIMITATIONS

1.	The discharge of waste through the San Elijo Ocean Outfall shall not, by itself or jointly with any other discharge, cause violation of the following Ocean Plan ocean water quality objectives.  Compliance with the water quality objectives shall be determined from samples collected at stations representative of the area within the waste field where initial dilution is completed.

a.	Bacterial Characteristics

(1)	Water-Contact Standards

Within a zone bounded by the shoreline and a distance of 1,000 feet from the shoreline or the 30-foot depth contour, whichever is further from the shoreline, and in areas outside this zone used for water-contact sports, as determined by the Regional Board, but including all kelp beds, the following bacterial objectives shall be maintained throughout the water column:

(a)	Samples of water from each sampling station shall have a density of total coliform organisms less than 1,000 per 100 ml (10 per ml); provided that not more than 20 percent of the samples at any sampling station, in any 30-day period, may exceed 1,000 per 100 ml (10 per ml), and provided further that no single sample when verified by a repeat sample taken within 48 hours shall exceed 10,000 per 100 ml (100 per ml).

(b)	The fecal coliform density based on a minimum of not less than five samples for any 30-day period, shall not exceed a geometric mean of 200 per 100 ml nor shall more than 10 percent of the total samples during any 60-day period exceed 400 per 100 ml.

The "Initial Dilution Zone" of wastewater outfalls shall be excluded from designation as kelp beds for purposes of bacterial standards.  Adventitious assemblages of kelp plants on waste discharge structures (e.g., outfall pipes and diffusers) do not constitute kelp beds for purposes of bacterial standards.  Kelp beds, for the purpose of the bacterial standards of this Order, are significant aggregations of marine algae of the genera Macrocystis and Nereocystis.  Kelp beds include the total foliage canopy of Macrocystis and Nereocystis plants throughout the water column.

(2)	Shellfish Harvesting Standards

At all areas where shellfish may be harvested for human consumption, as determined by the Regional Board, the following bacterial objectives shall be maintained throughout the water column:

The median total coliform density shall not exceed 70 per 100 ml, and not more than 10 percent of the samples shall exceed 230 per 100 ml.

b.	Bacterial Assessment and Remedial Action Requirements

The requirements listed below shall be used to 1) determine the occurrence and extent of any impairment of a beneficial use due to bacterial contamination; 2) generate information which can be used in the development of an enterococcus standard; and 3) provide the basis for remedial actions necessary to minimize or eliminate any impairment of a beneficial use.

Measurement of enterococcus density shall be conducted at all stations where measurement of total and fecal coliforms are required.  In addition to the requirements of Receiving Water Limitation C.1.a of this Order, if a shore station consistently exceeds a coliform objective or exceeds a geometric mean enterococcus density of 24 organisms per 100 ml for a 30-day period or 12 organisms per 100 ml for a six-month period, the Regional Board shall require the discharger to conduct or participate in a survey to determine the source of the contamination.  The geometric mean shall be a moving average based on no less than five samples per month, spaced evenly over the time interval.  When a sanitary survey identifies a controllable source of indicator organisms associated with a discharge of sewage, the Regional Board may require the discharger and any other responsible parties identified by the Regional Board to take action to control the source.

c.	Physical Characteristics

(1)		Floating particulates and grease and oil shall not be visible.

(2)		The discharge of waste shall not cause aesthetically undesirable discoloration of the ocean surface.

(3)		Natural light shall not be significantly reduced at any point outside the initial dilution zone as a result of the discharge of waste.

(4)		The rate of deposition of inert solids and the characteristics of inert solids in ocean sediments shall not be changed such that benthic communities are degraded.

d.	Chemical Characteristics

(1)		The dissolved oxygen concentration shall not at any time be depressed more than 10 percent from that which occurs naturally, as a result of the discharge of oxygen-demanding waste materials.

(2)		The pH shall not be changed at any time more than 0.2 units from that which occurs naturally.

(3)		The dissolved sulfide concentration of waters in and near sediments shall not be significantly increased above that present under natural conditions.

(4)		The concentration of substances, set forth in Receiving Water Limitation C.3 of this Order, in marine sediments shall not be increased to levels which would degrade indigenous biota.

(5)		The concentration of organic materials in marine sediments shall not be increased to levels that would degrade marine life.

(6)		Nutrient materials shall not cause objectionable aquatic growths or degrade indigenous biota.

e.	Biological Characteristics

(1)		Marine communities, including vertebrate, invertebrate, and plant species, shall not be degraded.

(2)		The natural taste, odor, and color of fish, shellfish, or other marine resources used for human consumption shall not be altered.

(3)		The concentration of organic materials in fish, shellfish, or other marine resources used for human consumption shall not bioaccumulate to levels that are harmful to human health.

f.	Radioactivity

Discharge of radioactive waste shall not degrade marine life.

2.	The discharge of waste through the San Elijo Ocean Outfall shall not, by itself or jointly with any other discharge, cause violation of the following Basin Plan ocean water quality objectives:

a.	The mean annual dissolved oxygen concentration shall not be less than 7.0 mg/L nor shall the minimum dissolved oxygen concentration be reduced below 5.0 mg/L at any time.

b.	The pH value shall not be depressed below 7.0 nor raised above 8.6.

3.	Toxic Materials

The discharge through the San Elijo Ocean Outfall shall not by itself or jointly with any other discharge, cause the following Ocean Plan water quality objectives to be exceeded in the receiving water upon completion of initial dilution, except that limitations indicated for radioactivity shall apply directly to the undiluted waste effluent.

a.	Water Quality Objectives for the Protection of Marine Aquatic Life

| Constituent | Units | 6 Month Median | Daily Maximum | Instantaneous Maximum |
| --- | --- | --- | --- | --- |
| arsenic | ug/L | 8 | 32 | 80 |
| cadmium | ug/L | 1 | 4 | 10 |
| chromium (hexavalent) | ug/L | 2 | 8 | 20 |
| copper | ug/L | 3 | 12 | 30 |
| lead | ug/L | 2 | 8 | 20 |
| mercury | ug/L | 0.04 | 0.16 | 0.4 |
| nickel | ug/L | 5 | 20 | 50 |
| selenium | ug/L | 15 | 60 | 150 |
| silver | ug/L | 0.45 | 1.8 | 4.5 |
| zinc | ug/L | 20 | 80 | 200 |
| cyanide | mg/L | 0.001 | 0.004 | 0.010 |
| total chlorine residual | mg/L | 0.002 | 0.008 | 0.060 |
| ammonia (as N) | mg/L | 0.60 | 2.4 | 6.0 |
| chronic toxicity | TUc | -- | 1 | -- |
| phenolic compounds (non-chlorinated) | mg/L | 0.030 | 0.12 | 0.30 |
| chlorinated phenolics | mg/L | 0.001 | 0.004 | 0.010 |
| Endosulfan7 | ug/l | 0.009 | 0.018 | 0.027 |
| endrin | ug/l | 0.002 | 0.004 | 0.006 |
| HCH8 | ug/l | 0.004 | 0.008 | 0.012 |
| Radioactivity9 | Not to exceed limits specified in Title 17, Division 1, Chapter 5, Subsection 4, Group 3, Article 1, Section 30253 of the California Code of Regulations. |  |  |  |  |  |  |

b.	Water Quality Objectives for the Protection of Human Health -- Noncarcinogens

| Chemical | Units | 30-Day Average |
| --- | --- | --- |
| acrolein | ug/L | 220 |
| antimony | ug/L | 1,200 |
| bis(2-chloroethoxy)methane | ug/L | 4.4 |
| bis(2-chloroisopropyl)ether | ug/L | 1,200 |
| chlorobenzene | ug/L | 570 |
| chromium (III) | ug/L | 190,000 |
| di-n-butyl phthalate | ug/L | 3,500 |
| Dichlorobenzenes10 | ug/L | 5,100 |
| 1,1-dichloroethylene | ug/L | 7,100 |
| diethyl phthalate | ug/L | 33,000 |
| dimethyl phthalate | ug/L | 820,000 |
| 4,6-dinitro-2-methylphenol | ug/L | 220 |
| 2,4-dinitrophenol | ug/L | 4.0 |
| ethylbenzene | ug/L | 4,100 |
| fluoranthene | ug/L | 15 |
| hexachlorocyclopentadiene | ug/L | 58 |
| isophorone | ug/L | 150,000 |
| nitrobenzene | ug/L | 4.9 |
| thallium | ug/L | 14 |
| toluene | ug/L | 85,000 |
| 1,1,2,2-tetrachloroethane | ug/L | 1,200 |
| tributyltin | ug/l | 0.0014 |
| 1,1,1-trichloroethane | ug/L | 540,000 |
| 1,1,2-trichloroethane | ug/L | 43,000 |

c.	Water Quality Objectives for the Protection of Human Health -- Carcinogens

| Chemical | Units | 30-Day Average |
| --- | --- | --- |
| acrylonitrile | ug/L | 0.10 |
| aldrin | ug/l | 0.000022 |
| benzene | ug/L | 5.9 |
| benzidine | ug/l | 0.000069 |
| beryllium | ug/l | 0.033 |
| bis(2-chloroethyl)ether | ug/L | 0.045 |
| bis(2-ethylhexyl)phthalate | ug/L | 3.5 |
| carbon tetrachloride | ug/L | 0.90 |
| chlordane11 | ug/l | 0.000023 |
| chloroform | ug/L | 130 |
| DDT12 | ug/l | 0.00017 |
| 1,4-dichlorobenzene | ug/L | 18 |
| 3,3-dichlorobenzidine | ug/l | 0.0081 |
| 1,2-dichloroethane | ug/L | 130 |
| dichloromethane | ug/L | 450 |
| 1,3-dichloropropene | ug/L | 8.9 |
| dieldrin | ug/l | 0.000040 |
| 2,4-dinitrotoluene | ug/L | 2.6 |
| 1,2-diphenylhydrazine | ug/L | 0.16 |
| Halomethanes13 | ug/L | 130 |
| Heptachlor14 | ug/l | 0.00072 |
| hexachlorobenzene | ug/l | 0.00021 |
| hexachlorobutadiene | ug/L | 14 |
| hexachloroethane | ug/L | 2.5 |
| Chemical | Units | 30-Day Average |
| N-nitrosodimethylamine | ug/L | 7.3 |
| N-nitrosodiphenylamine | ug/L | 2.5 |
| PAHs15 | ug/l | 0.0088 |
| PCBs16 | ug/l | 0.000019 |
| TCDD equivalents17 | pg/l | 0.0039 |
| tetrachloroethylene | ug/L | 99 |
| toxaphene | ug/l | 0.00021 |
| trichloroethylene | ug/L | 27 |
| 2,4,6-trichlorophenol | ug/L | 0.29 |
| vinyl chloride | ug/L | 36 |

mg/L = milligrams per liter

ug/L = micrograms per liter

ng/l = nanograms per liter

pg/l = picograms per liter

NTU = Nephelometric Turbidity Unit

TUc = toxic units chronic

D.	PRETREATMENT REQUIREMENTS

1.	The discharger shall conduct a semi-annual Industrial Waste Survey (IWS) of all the Industrial Users (IUs) in the service area of the San Elijo Water Reclamation Facility (SEWRF) in order to determine whether any such IUs are subject to pretreatment standards specified in 40 CFR 403.  The discharger shall also conduct a semi-annual priority pollutant scan of the SEWRF effluent.  Based on the results of the IWS, the priority pollutant scan, and review of 40 CFR 403,  the discharger shall submit a semi-annual certification report indicating whether the SEWRF receives pollutants from any IU which would require the discharger to establish a pretreatment program in accordance with 40 CFR 403.  The semi-annual certification reports, with the IWS and sampling results, shall be submitted no later than February 1st and August 1st of each year.  If, and when, the discharger becomes aware of an IU in the service area of the SEWRF which would require the San Elijo Joint Powers Authority to establish a pretreatment program pursuant to 40 CFR 403, the discharger shall notify the Regional Board requesting a modification of this Order and shall develop and implement a pretreatment program in accordance with the requirements of Sections 307(b) and (c), and 402(b)(8) of the CWA and 40 CFR 403. The discharger shall assure that IUs in the service area of the SEWRF subject to pretreatment standards promulgated in federal regulations or established by the discharger comply with those standards.

2.	The Regional Board may amend this Order, at any time, to require the discharger to develop and implement an industrial pretreatment program pursuant to the requirements of 40 CFR 403, if the Regional Board finds that the SEWRF receives pollutants from an industry which is subject to pretreatment standards or if other circumstances warrant doing so.

3.	The SEJPA is comprised of two member agencies, the City of Solana Beach, and the Cardiff Sanitation District (City of Encinitas).  These agencies provide programs that protect the sewer system from disposal of toxic materials.  These programs and activities implemented by the member agencies constitute the Nonindustrial Source Control Program.  To ensure continued protection of the sewer system, the SEJPA shall review the sewer protection programs implemented by the agencies and submit a written report at least once before the expiration date of this Order.

E.	SLUDGE REQUIREMENTS

1.	Management of all solids and sludge must comply with all requirements of CFR Parts 257, 258, 501, and 503, including all monitoring, record-keeping, and reporting requirements.  Since the State of California, hence the Regional and State Boards, has not been delegated the authority by the USEPA to implement the sludge program, enforcement of sludge requirements of CFR Part 503 is under USEPA's jurisdiction.

2.	All solids and sludge must be disposed of in a municipal solid waste landfill, reused by land application, or disposed of in a sludge-only landfill in accordance with 40 CFR Parts 503 and 258, and Title 23 CCR Chapter 15.  If the discharger desires to dispose of solids or sludge by a different method, a request for permit modification must be submitted to the USEPA and this Regional Board 180 days prior to the alternative disposal.

3.	Sludge that is disposed of in a municipal solid waste landfill must meet the requirements of 40 CFR 25.  In the annual self-monitoring report, the discharger shall include the amount of sludge disposed of, and the landfill(s) to which it was sent.

4.	All the requirements of 40 CFR 503 and 23 CCR 15 are enforceable by the USEPA and this Regional Board whether or not the requirements are stated in an NPDES permit or any other permit issued to the discharger.

5.	The discharger shall take all reasonable steps to prevent and minimize any sludge use or disposal in violation of this Order that has a likelihood of adversely affecting human health or the environment.

6.	Solids and sludge treatment, storage, and disposal or reuse shall not create a nuisance, such as objectionable odors or flies, and shall not result in groundwater contamination.

7.	The solids and sludge treatment and storage site shall have facilities adequate to divert surface water runoff from adjacent areas, to protect the boundaries of the site from erosion, and to prevent drainage from the treatment and storage site.  Adequate protection is defined as protection from at least a 100-year storm and protection from the highest possible tidal stage that may occur.

8.	The discharge of sewage sludge and solids shall not cause waste material to be in a position where it is, or can be, conveyed from the treatment and storage sites and deposited in the waters of the state.

9.	The discharger shall submit an annual report to the USEPA and this Regional Board containing monitoring results and pathogen and vector attraction reduction requirements, as specified by 40 CFR 503.  The discharger shall also report the quantity of sludge disposed and the disposal method.  This self-monitoring report must be postmarked by February 19th of each year and report for the period covering the previous calendar year.

F.	PROVISIONS

1.	The discharger must comply with all standard provisions, where applicable, as stated in 40 CFR 122.41 (Attachment 3) and Attachment 4.

2.	The following sections of 40 CFR (Attachment 5) are incorporated into this permit by reference, and the discharger must comply with these provisions:

a)122.5		Effect of a permit

b)122.21		Application for a permit

c)122.22		Signatories to permit applications and reports

d)122.61		Transfer of permits

e)122.62		Modification or revocation of permits

f)122.63		Minor modifications of permits

g)122.64		Termination of permits

3.	This Order may be modified, revoked and reissued, or terminated for causes including, but not limited to, the following:

a.	Violation of any terms or conditions of this Order.

b.	Obtaining this Order by misrepresentation or failure to disclose fully all relevant facts.

c.	A change in any condition that requires either a temporary or permanent reduction or elimination of the authorized discharge.

4.	If any applicable toxic effluent standard or prohibition (including any schedule of compliance specified in such effluent standard or prohibition) is promulgated under Section 307(a) of the CWA for a toxic pollutant and that standard or prohibition is more stringent than any limitation on the pollutant in this Order, the Executive Officer may institute proceedings under these regulations to modify or revoke and reissue the Order to conform to the toxic effluent standard or prohibition.

5.	The discharger shall comply with effluent standards or prohibitions established under Section 307(a) of the CWA for toxic pollutants and with standards for sewage sludge use and disposal established under Section 405(d) of the CWA within the time provided in the regulations that establish those standards or prohibitions or standards for sewage sludge use or disposal, even if this Order has not yet been modified to incorporate the requirement.

6.	The discharger shall comply with all existing federal and state laws and regulations that apply to its sewage sludge use and disposal practice(s), and with the CWA Section 405(d) and 40 CFR Part 257.

7.	This Order does not convey any property rights of any sort or any exclusive privilege.  The requirements prescribed herein do not authorize the commission of any act causing injury to persons or property, nor protect the discharger from its liabilities under federal, state, or local laws, nor create a vested right for the discharger to continue its waste discharge.

8.	It shall not be a defense for the discharger in an enforcement action that it would have been necessary to halt or reduce the permitted activity in order to maintain compliance with the conditions of this Order.  Upon reduction, loss, or failure of a treatment facility, the discharger shall, to the extent necessary to maintain compliance with this Order, control all discharges until the facility is restored or an alternative method of treatment is provided.  This provision applies, for example, when the primary source of power of a treatment facility fails, is reduced, or is lost.

9.	Supervisors and operators of the discharger's wastewater treatment facilities shall possess a certificate of appropriate grade in accordance with Chapter 14 of Division 4 of Title 23 of the California Code of Regulations.

10.	The discharger's wastewater treatment facilities shall be operated and maintained in accordance with the operation and maintenance manual(s) prepared by the discharger through the Clean Water Grant Program.

11.	A copy of this Order shall be posted at a prominent location at or near the treatment and disposal facilities, and shall be available to operating personnel at all times.

12.	The discharger shall comply with any interim effluent limitations as established by an addendum, enforcement action or revised waste discharge requirements which have been or may be adopted by this Regional Board.

13.	All proposed new treatment facilities and expansions of existing treatment facilities shall be completely constructed and operable prior to initiation of the discharge from the new or expanded facilities.  The discharger shall submit a certification report for each new treatment facility, expansion of an existing treatment facility, and re-rating of an existing treatment facility.  For new treatment facilities and expansions, the certification report shall be prepared by the design engineer.  For re-ratings, the certification report shall be prepared by the engineer who evaluated the treatment facility capacity.  The certification report shall:

a.	Identify the design capacity of the treatment facility;

b.	Certify the adequacy of each component of the treatment facility; and

c.	Contain a requirement-by-requirement analysis, based on acceptable engineering practices, of how the process and physical design of the facility will ensure compliance with this Order.

The signature and engineering license number of the engineer preparing the certification report shall be affixed to the report.  The certification report, should, if possible, be submitted prior to beginning construction.  The discharger shall not initiate a discharge from a new treatment facility or initiate a discharge from an existing treatment facility at a 30-day average dry weather flowrate in excess of its previously approved design capacity until:

a.	The certification report is received by the Executive Officer;

b.	The Executive Officer has received written notification of the completion of construction (new treatment facilities and expansions only);

c.	An inspection of the plant has been made by the Regional Board staff (new treatment facilities and expansions only); and

d.	The Executive Officer has provided the discharger with written authorization to discharge at a 30-day average dry weather flowrate not to exceed the revised design capacity.

14.	If only one sample is collected during the time period associated with the effluent limitations (e.g., 30-day average or 6-month median), the single measurement shall be used to determine compliance with the effluent limitation for the entire time period.

15.	All analytical data shall be reported uncensored with detection limits and quantitation limits identified.  For any effluent limitation, compliance shall be determined using appropriate statistical methods to evaluate multiple samples.  Sufficient sampling and analysis shall be conducted to determine compliance.

16.	Compliance based on a single sample analysis shall be determined where appropriate as described below.

a.	When a calculated effluent limitation is greater than or equal to the PQL (defined below), compliance shall be determined based on the calculated effluent limitation and either single or multiple sample analyses.

b.	When the calculated effluent limitation is below the PQL, compliance determinations based on analysis of a single sample shall only be undertaken if the concentration of the constituent of concern in the sample is greater than or equal to the PQL.

c.	When the calculated effluent limitation is below the PQL and recurrent analytical responses between the PQL and the calculated limit occur, compliance shall be determined by statistical analysis of multiple samples.

17.	Published values for MDLs (defined below) and PQLs should be used except where revised MDLs and PQLs are available from recent laboratory performance evaluations, in which case the revised MDLs and PQLs should be used.  Where published values are not available, the Executive Officer will determine appropriate values based on available information, including information submitted by the discharger upon request of the Executive Officer.

a.	The Method Detection Limit (MDL) is the minimum concentration of a substance that can be measured and reported with 99% confidence that the analyte concentration is greater than zero, as defined in 40 CFR Part 136 Appendix B.

b.	The Practical Quantitation Level (PQL) is the lowest concentration of a substance which can be consistently determined within +/-20% of the true concentration by 75% of the labs tested in a performance evaluation study.  Alternatively, if performance data are not available, the PQL for carcinogens is the MDL x 5, and for noncarcinogens is the MDL x 10.

18.	When determining compliance based on a single sample, with a single effluent limitation which applies to a group of chemicals (e.g., PCBs) concentrations of individual members of the group may be considered to be zero if the analytical response for individual chemicals falls below the MDL for that parameter.

19.	The 6-month median effluent concentration limitation shall apply as a moving median of daily values for any 180-day period in which daily values represent flow-weighted average concentrations within a 24-hour period.  For intermittent discharges, the daily value shall be considered to equal zero for days on which no discharge occurred.  The 6-month median receiving water limitation shall apply as a moving median of all values collected for any 180-day period.

20.	The 30-day average effluent limitation shall be the moving arithmetic mean of daily concentrations over the specified 30-day period.

21.	The 7-day average shall be the moving arithmetic mean of daily concentrations over the specified 7-day period.

22.	The daily maximum effluent limitation shall apply to flow-weighted 24-hour composite samples.  The daily maximum receiving water limitation shall apply to grab sample determinations.

23.	The instantaneous maximum effluent limitation shall apply to grab sample determinations.  The instantaneous maximum receiving water limitation shall apply to grab sample determinations.

24.	The mass emission rate (MER), in pounds per day, shall be obtained from the following calculation for any calendar day:

mass emission rate (lb/Day) = 8.34 x Q x C

in which Q and C are the flow rate in MGallons/ Day and the constituent concentration in mg/L, respectively, and 8.34 is a conversion factor.  If a composite sample is taken, then C is the concentration measured in the composite sample and Q is the average flow rate occurring during the period over which the samples are composited.

25.	Compliance with the Acute Toxicity limitation in Discharge Specification B.1.a. of this Order shall be determined using an established protocol, e.g., American Society for Testing Materials (ASTM), USEPA, American Public Health Association, or State Board.  Acute Toxicity (TUa) shall be expressed in Toxic Units Acute (TUa), where:

TUa =         100

96-hour LC50

Where LC50 is the Lethal Concentration 50% and the percent waste giving 50% survival of test organisms.  LC50 shall be determined by static or continuous flow bioassay techniques using standard test species.  If specific identifiable substances in wastewater can be demonstrated by the discharger as being rapidly rendered harmless upon discharge to the marine environment, but not as a result of dilution, the LC 50 may be determined after the test samples are adjusted to remove the influence of those substances.

When it is not possible to measure the 96-hour LC50 due to greater than 50% survival of the test species in 100% waste, the toxicity concentration shall be calculated by the following:

TUa = log (100 - S)

1.7

where S is the percentage survival in 100% waste. If S > 99, TUa shall be reported as zero.

26.	Compliance with the Chronic Toxicity effluent limitation established in Discharge Specification No. B.1.b of this Order shall be determined using critical life stage toxicity tests.  Chronic Toxicity (TUc) shall be expressed as Toxic Units Chronic (TUc), where:

TUc = 100

NOEL

where NOEL is the No Observed Effect Level and is expressed as the maximum percent effluent that causes no observable effect on a test organism, as determined by the result of a critical life stage toxicity test listed below.

A minimum of three test species with approved test protocols shall be used to measure compliance with the chronic toxicity objective.  If possible, the test species shall include a fish, an invertebrate, and an aquatic plant.  After a screening period, monitoring may be reduced to the most sensitive species.  Dilution and control water should be obtained from an unaffected area of the receiving waters.  The sensitivity of the test organisms to a reference toxicant shall be determined concurrently with each bioassay test and reported with the test results.

The tests specified in the July 1997 Ocean Plan shall be used to measure TUc.  Other tests may be added to the list when approved by the SWRCB.

27.	If toxicity testing results show a violation of any acute or chronic toxicity limitation identified in Discharge Specification B.1 of this Order, the discharger shall:

a.	Take all reasonable measures necessary to immediately minimize toxicity; and

b.	Increase the frequency of the toxicity test(s) that showed a violation to at least two times per month until the results of at least two consecutive toxicity tests do not show violations.

If the Executive Officer determines that toxicity testing shows consistent violation of any acute or chronic toxicity limitation identified in Discharge Specification B.1. of this Order, the discharger shall conduct a Toxicity Reduction Evaluation (TRE) which includes all reasonable steps to identify the source of toxicity.  Once the source of toxicity is identified, the discharger shall take all reasonable steps to reduce the toxicity to meet the toxicity limitations identified in Discharge Specification B.1 of this Order.

Within fourteen days of completion of the TRE, the discharger shall submit the results of the TRE, including a summary of the findings, data generated, a list of corrective actions necessary to achieve consistent compliance with all the toxicity limitations of this Order and prevent recurrence of violations of those limitations, and a time schedule for implementation of such corrective actions.  The corrective actions and time schedule shall be modified at the direction of the Executive Officer.

28.	For all bacterial analyses, sample dilutions should be performed so the range of values extends from 2 to 16,000 MPN (most probable number). The detection methods used for each analysis shall be reported with the results of the analysis.  Detection methods used for coliforms (total and fecal) shall be those presented in the most recent edition of Standard Methods for the Examination of Water and Wastewater or any improved method determined by the Regional Board (and approved by USEPA) to be appropriate.  Detection methods used for enterococcus shall be those presented in USEPA publication USEPA 600/4-85/076, Test Methods for Escherichia coli and Enterococci in Water By Membrane Filter Procedure or any improved method determined by the Regional Board to be appropriate.

29.	The geometric mean used for determining compliance with bacterial standards is calculated with the following equation:

Geometric Mean = (C1 x C2 x ... x Cn) 1/n

where n is the number of days samples were collected during the period and C is the concentration of bacteria (MPN/100 mL) found on each day of sampling.

30.	As used in this Order, waste includes a discharger's total discharge, of whatever origin (i.e. gross, not net, discharge).

31.	Reduction of natural light may be determined by the Regional Board by measurement of light transmissivity or total irradiance, or both, according to the monitoring needs of the Regional Board.

32.	The discharger shall maintain a Sewer Overflow Prevention Plan (SOPP) in an up-to-date condition and shall amend the SOPP whenever there is a change (e.g. in the design, construction, operation, or maintenance of the sewerage system or sewerage facilities) which materially affects the potential for sewer overflows.  The discharger shall review and amend the SOPP as appropriate after each sewer overflow from the SEOO or in the service area of the SEWRF.  The SOPP and any amendments thereto, shall be subject to the approval of the Executive Officer and shall be modified as directed by the Executive Officer.  The discharger shall submit the SOPP and any amendments thereto to the Executive Officer upon request of the Executive Officer.  The discharger shall ensure that the up-to-date SOPP is readily available to sewerage system personnel at all times and that sewerage system personnel are familiar with it.

- The discharger shall maintain a Sewer Overflow Response Plan (SORP) for the SEOO and the service area of the SEWRF.  The SORP shall establish procedures for responding to sewer overflows from the SEOO and to sewer overflows in the service area of the SEWRF so as to (a) minimize the sewer overflow volume which enters surface waters, and (b) minimize the adverse effects of sewer overflows on water quality and beneficial uses.  The discharger shall maintain the SORP in an up-to-date condition and shall amend the SORP as necessary to accomplish these objectives.  The discharger shall review and amend the SORP as appropriate after each sewer overflow from the SEOO or in the service area of the SEWRF.  The SORP, and any amendments thereto, shall be subject to the approval of the Executive Officer and shall be modified as directed by the Executive Officer.  The discharger shall submit the SORP and any amendments thereto to the Executive Officer upon request of the Executive Officer.  The discharger shall ensure that the up-to-date SORP is readily available to sewerage system personnel at all times and that sewerage system personnel are familiar with it.

34.	No later than 10 months after the adoption of this Order, the discharger shall submit a written report to the Executive Officer, addressing the following:

a.	Most current information on the capacity of the San Elijo Ocean Outfall.

b.	The dischargers’ best estimate of when the average daily dry-weather flow will equal or exceed the SEOO capacity.

c.	The dischargers’ intended schedule for studies, design, and other steps needed to provide additional capacity for the SEOO and/or to control the flowrate before the flowrate is equal to the current outfall capacity.

d.	The report must be signed, and agreed upon by each of the parties discharging to the SEOO.

G.	REPORTING REQUIREMENTS

1.	The discharger must comply with standard monitoring and reporting requirements, where applicable, as stated in 40 CFR 122.41 (Attachment 3) and Attachment 4.

- This Order expires November 10, 2004.  If the discharger wishes to continue an activity regulated by this Order after the expiration date of this Order, the discharger must apply for and obtain new waste discharge requirements.  The discharger must submit a full and complete Report of Waste Discharge in accordance with Title 23 of the California Code of Regulations, to the Executive Officer, not later than 180 days in advance of the expiration date of this Order, as application for issuance of new waste discharge requirements. Not less than 180 days prior to any material change in the character, location, volume, or amount of waste discharge, the Discharger shall submit a technical report describing such changes.  Such changes include but are not limited to the following:

- Addition of a major industrial waste discharge to a discharge of essentially domestic sewage, or the addition of a new process or product by an industrial facility resulting in a change in the character of the waste.

- Significant change in disposal method, e.g., change from land disposal to a direct discharge to water, or change in the method of treatment which would significantly alter the characteristics of the waste.

- Significant change in the disposal area, e.g., moving the discharge to another drainage area, to a different water body, or to a disposal area significantly removed from the original area potentially causing different water quality or nuisance problems.

- Increase in flow beyond that specified in the waste discharge requirements.

- Increase in area or depth to be used for solid waste disposal beyond that specified in the waste discharge requirements. [CWC  13372, 13376, 13264, 23 CCR 2210]

- Any substantial change in the amount or characteristics of pollutants used, handled, stored, or generated.

- Any new discharge of pollutants or new potential pollutant source.

- Other circumstances which could result in a material change in the character, amount, or location of discharges. [CWC  13372, 13264,23 CCR 2210]

3.	Pursuant to State Board Order No. WQ 84-7, the discharger shall submit with its Report of Waste Discharge for reissuance of its NPDES permit, sufficient information to justify why any effluent proposed to be discharged to the ocean is not being reclaimed for beneficial use.

4.	The discharger shall report sewer overflow events in accordance with the following procedures:

a.	All sewer overflow events that occur in the service area of the SEWRF shall be reported to the Regional Board and the County of San Diego Department of Environmental Health Services.  A sewer overflow event is a discharge of treated or untreated wastewater at a location not authorized by waste discharge requirements and/or NPDES permit which results from a pump station failure, sewer line break, obstruction, surcharge, or any other circumstance.

b.	If a sewer overflow event results in a discharge to surface waters:

(1)	The sewer overflow event shall be reported to the Regional Board and the County of San Diego Environmental Health Services by telephone within 24 hours of the time the discharger becomes aware of the sewer overflow event.  The telephone report shall include only the information specified by Item Nos. 1 through 5, 8, 12 A, 12 B and 13 contained in the Sewer Overflow Report (SOR) form supplied by the Regional Board.

(2)	An SOR form (completed in accordance with the instructions), as well as any additional pertinent information, shall be submitted to the Regional Board no later than five days following the starting date of the sewer overflow event.

c.	If a sewer overflow event does not result in a discharge to surface waters:

(1)	No telephone report is required.

(2)	A SOR form (completed in accordance with the instructions), as well as any additional pertinent information, shall be submitted to the Regional Board no later than five days following the starting date of the sewer overflow event.

5.	The discharger shall provide adequate notice to the Executive Officer of the following:

a.	Any new introduction of pollutants into the discharger's treatment works from an indirect discharger which would be subject to Section 301 or 306 of the CWA if it were directly discharging those pollutants;

b.	Any substantial change in the volume or character of pollutants being introduced into the discharger's treatment works by a source introducing pollutants into the treatment works at the time of issuance of this Order; and

c.	For purposes of this paragraph, adequate notice shall include information on:

(1)	The quality and quantity of effluent introduced into the POTW, and

(2)	Any anticipated impact of the change on the quantity or quality of effluent and/or sludge to be discharged from the POTW.

6.	Whenever a receiving water sample is found to contain levels of bacteria which exceed bacterial water quality objectives specified in Receiving Water Limitation C.1.a. (1) of this Order, the discharger shall immediately notify the County of San Diego Department of Environmental Health Services and post signs prohibiting body contact with the water in all areas affected by the contamination.

7.	Reports of compliance or noncompliance with, or any progress reports on, interim and final requirements contained in any compliance schedule of this permit shall be submitted no later than 14 days following each schedule date.

8.	The discharger shall submit a written report to the Executive Officer within 90 days after the average dry weather influent flowrate for any 30-day period equals or exceeds 75 percent of the design capacity of the waste treatment and/or disposal facilities.  The discharger's senior administrative officer shall sign a letter which transmits that report and certifies that the policy-making body is adequately informed about it.  The report shall include:

a.	Average daily flow for the 30-day period, the date on which the instantaneous peak flow occurred, the rate of that peak flow, and the total flow for that day.

b.	The discharger's best estimate of when the average daily dry-weather flowrate will equal or exceed the design capacity of the facilities.

c.	The discharger's intended schedule for studies, design, and other steps needed to provide additional capacity for the waste treatment and/or disposal facilities and/or control the flowrate before the waste flowrate equals the capacity of present units.

9.	Except for data determined to be confidential under 40 CFR Part 2, all reports prepared in accordance with the terms of this Order shall be available for public inspection at the offices of the California Regional Water Quality Control Board, San Diego Region.  As required by the CWA, Reports of Waste Discharge, this Order, and effluent data shall not be considered confidential.

10.	The discharger shall submit reports and provide notifications to the Regional Board and other agencies as specified in this Order.  These other agencies include USEPA, and the San Diego County Department of Health Services.  Reports shall be submitted and notifications shall be made to:

a.	Executive Officer

California Regional Water Quality Control Board

San Diego Region

9771 Clairemont Mesa Boulevard, Suite A

San Diego, California  92124-1324

Phone - (858) 467-2952

Fax - (858) 571-6972

b.	Regional Administrator

U.S. Environmental Protection Agency

Region 9

75 Hawthorne Street

San Francisco, California  94105

c.		Environmental Health Services Division

Department of Health Services

County of San Diego

P.O. Box 85261

San Diego, California  92138-5261

Phone - (619) 338-2222

Fax - (619) 338-2174

H.	NOTIFICATIONS

1.	California Water Code Section 13263(g) states:

No discharge of waste into the waters of the state, whether or not such discharge is made pursuant to waste discharge requirements, shall create a vested right to continue such discharge.  All discharges of waste into waters of the state are privileges, not rights.

2.	The discharger is held accountable for responsibilities, liabilities, legal actions, and penalties as stated in Attachment 4 and Attachment 5 of this Order.

3.	This Order shall become effective 10 days after the date of its adoption provided the Regional Administrator, USEPA, has no objection.  If the Regional Administrator objects to its issuance, this Order shall not become effective until such objection is withdrawn.

4.	This Order supersedes Order No. 94-105 when this Order becomes effective.

ORDER NO. 99-71 ENDNOTES

Secondary treatment is defined by the USEPA Administrator in the federal regulations (40 CFR Part 133.100 to 40 CFR Part 133.105) in terms of three parameters: 5-day biochemical oxygen demand (BOD), total suspended solids (TSS), and pH.  Federal regulations allow substitution of 5-day carbonaceous biological demand (CBOD) limitations for BOD limitations.

Effluent concentration limitations are specified in the 1997 Ocean Plan, Table A.  Mass emission rate (MER) limitations, where applicable, were determined using procedures outlines in the Ocean Plan, equation 2, and a flowrate of 5.25 MGallons/ Day.

Effluent limitations were determined using the procedures outlined in the 1997 Ocean Plan, and an initial dilution of 220.   Mass emission rate (MER) limitations were determined using procedures outlined in the Ocean Plan, Equation 2, and a flowrate of 5.25 MGallons/ Day.

The discharger may, at its option, meet this limitation as a total chromium limitation.

If the discharger can demonstrate to the satisfaction of the Regional Board (subject to EPA approval) that an analytical method is available to reliably distinguish between strongly and weakly complexed cyanide, effluent limitations for cyanide may be met by the combined measurement of free cyanide, simple alkali metal cyanides, and weakly complexed organometallic cyanide complexes.  In order for the analytical method to be acceptable, the recovery of free cyanide from metal complexes must be comparable to that achieved by Standard Methods 412 F, G, and H (Standard Methods for the Examination of Water and Wastewater, Joint Editorial Board, American Public Health Association, American Water Works Association, and Water Pollution Control Federation, most recent edition.)

The effluent concentration and mass emission rate limitations for total chlorine residual are based on a continuous discharge of chlorine.  Effluent concentration limitations for total chlorine residual, which are applicable to intermittent discharges not exceeding 2 hours, shall be determined through the use of the following equations:

log Co = -0.43 (log x) + 1.8

Ce = Co + Dm (Co - Cs)

where:

Co	=  the concentration (in ug/L) to be met at the completion of initial dilution

x	=  the duration of uninterrupted chlorine discharge in minutes

Ce	=  the effluent concentration limitation ug/L to apply when chlorine is being intermittently discharged

Dm	=  the minimum probable initial dilution

Cs	=  the background seawater concentration = 0

Endosulfan shall mean the sum of endosulfan-alpha and -beta and endosulfan sulfate.

HCH shall mean the sum of the alpha, beta, gamma (lindane) and delta isomers of hexachlorocyclohexane.

The 1997 Ocean Plan refers to limits specified in Title 17, Division 5, Chapter 4, Group 3, Article 3, Section 32069 of the California Code of Regulations. This section has been repealed, and substituted with limitations set forth in this Order.

Dichlorobenzenes shall mean the sum of 1,2- and 1,3-dichlorobenzene.

Chlordane shall mean the sum of chlordane-alpha, chlordane-gamma, chlordene-alpha, chlordene-gamma, nonachlor-alpha, nonachlor-gamma, and oxychlordane.

DDT shall mean the sum of 4,4'DDT, 2,4'DDT, 4,4'DDE, 2,4'DDE, 4,4'DDD, and 2,4'DDD.

Halomethanes shall mean the sum of bromoform, bromomethane (methyl bromide), chloromethane (methyl chloride), chlorodibromomethane, and dichlorobromomethane.

Heptachlor shall mean the sum of heptachlor and heptachlor epoxide.

PAHs (polynuclear aromatic hydrocarbons) shall mean the sum of acenaphthylene, anthracene, 1,2-benzanthracene, 3,4-benzofluoranthene, benzo[k]fluoranthene, 1,12-benzoperylene, benzo[a]pyrene, chrysene, dibenzo[ah]anthracene, fluorene, indeno[1,2,3-cd]pyrene, phenanthrene and pyrene.

PCBs (polychlorinated biphenyls) shall mean the sum of chlorinated biphenyls whose analytical characteristics resemble those of Aroclor-1016, Aroclor-1221, Aroclor-1232, Aroclor-1242, Aroclor-1248, Aroclor-1254 and Aroclor-1260.

TCDD EQUIVALENTS shall mean the sum of the concentrations of chlorinated dibenzodioxins (2,3,7,8-CDDs) and chlorinated dibenzofurans (2,3,7,8-CDFs) multiplied by their respective toxicity factors, as shown in the table below.

Isomer Group			Toxicity Equivalence Factor

2,3,7,8-tetra CDD			1.0

2,3,7,8-penta CDD			0.5

2,3,7,8-hexa CDDs			0.1

2,3,7,8-hepta CDD			0.01

octa CDD				0.001

2,3,7,8 tetra CDF			0.1

1,2,3,7,8 penta CDF		0.05

2,3,4,7,8 penta CDF		0.5

2,3,7,8 hexa CDFs			0.1

2,3,7,8 hepta CDFs			0.01

octa CDF				0.001