CALIFORNIA REGIONAL WATER QUALITY CONTROL BOARD

SAN DIEGO REGION

ADDENDUM NO. 1

TO

ORDER NO. 99-47 AND 99-48

NPDES NO. CA0108073 AND CA0108181

WASTE DISCHARGE REQUIREMENTS

FOR

SOUTHERN CALIFORNIA EDISON COMPANY

SAN ONOFRE NUCLEAR GENERATING STATION, UNIT 2 AND UNIT 3

# SAN DIEGO COUNTY

The California Regional Water Quality Control Board, San Diego Region (hereinafter SDRWQCB), finds that:

- On August 11, 1999, the SDRWQCB adopted Order No. 99-47 National Pollutant Discharge Elimination System (NPDES) Permit No. CA0108073, WASTE DISCHARGE REQUIREMENTS FOR SOUTHERN CALIFORNIA EDISON COMPANY SAN ONOFRE NUCLEAR GENERATING STATION, UNIT 2 SAN DIEGO COUNTY.

- Also On August 11, 1999, the SDRWQCB adopted Order No. 99-48 National Pollutant Discharge Elimination System (NPDES) Permit No. CA0108181, WASTE DISCHARGE REQUIREMENTS FOR SOUTHERN CALIFORNIA EDISON COMPANY SAN ONOFRE NUCLEAR GENERATING STATION, UNIT 3 SAN DIEGO COUNTY.

- By letter dated December 10, 1999, Southern California Edison (SCE) requested permission to discharge wastes generated at the Unit No. 1 facility through the Unit Nos. 2 and/or 3 outfalls.  The Unit Nos. 2 and 3 permits currently contain provisions for the discharge from the two on-site wastewater treatment plants through either the Unit No. 2 and/or 3 outfall.  This addendum modifies Order Nos. 99-47 and 99-48 to allow the discharge of all in-plant waste sources generated at Unit No. 1 through either the Unit No. 2 and/or 3 outfall.

4.	In addition, this addendum modifies Order Nos. 99-47 and 99-48 to specifically incorporate the guidance and provisions established in two paragraphs on page 13 of the Water Quality Control Plan for Ocean Waters of California, 1997 (Ocean Plan).  Chapter IV, Part B of the Ocean Plan on the fourth paragraph of page thirteen provides specific guidance on the application of Ocean Plan effluent limits and certain monitoring requirements.  The existing Orders do not contain provisions for the creation of a sample consisting of all the in-plant waste streams, nor were the limits applied as required by the Ocean Plan.  This addendum establishes both modified and additional effluent limitations and monitoring requirements in accordance with the Ocean Plan requirement.

5.	This addendum also modifies the toxicity reduction evaluation (TRE) implementation procedures to reflect the guidance contained within the Ocean Plan.  Chapter IV, Part C of the Ocean Plan on the fifth paragraph of page 13 provides guidance on toxicity reduction evaluation (TRE) requirements.  This addendum deletes the original TRE provision in Order Nos. 99-47 and 99-48 and modifies a Monitoring and Reporting Program provision so that a consistent toxic result is required prior to the implementation of the TRE. The existing orders required the implementation of a TRE immediately after a toxicity test result exceeded an effluent limitation.

- This addendum also changes the location of three control stations to the receiving water monitoring and reporting program that is shared by Unit Nos. 2 and 3.  The modification will improve the usefulness of the deep-water turbidity data.

- Finally, this addendum modifies the due dates for monitoring reports to be consistent with other NPDES permits and the Water Quality Standards Team Final Report, State Water Resources Control Board, April, 1999.

- The San Onofre Nuclear Generating Station (SONGS) consists of three discrete operating units, each with a separate intake and discharge structure.  Unit No. 1 is the oldest of the three.  Originally put into operation in 1968, Unit No. 1 passed a maximum of 460.8 million gallons per day (Mgallons/Day) of cooling water through its condensers until it was shutdown in 1992.  SCE was allowed to begin decommissioning the plant around July 1999.  The process should continue through 2004.  The Unit No. 1 intake structure is located approximately 2,980 feet offshore and is fitted with a velocity cap.  The outfall is approximately 2,460 feet offshore and is similar in design to the intake structure except without a cap.  The Ocean Plan dilution factor assigned to that outfall is 2.4.  The fate of the Unit No. 1 outfall and intake structures is currently under consideration.  In anticipation of the removal of those structures, SCE has requested permission to discharge Unit No. 1 wastes through the Unit Nos. 2 and 3 outfalls.

9.	SONGS Unit No. 2 and 3 are currently producing electrical power.  Each Unit passes a maximum of 1218.6 Mgallons/Day of cooling water through its condensers.  The SONGS Unit No. 2 intake is located 3,183 feet offshore.  The Unit No. 2 outfall extends along an extensive diffuser array from 5,888 feet to 8,350 feet offshore.  The Unit No. 3 intake structure is 3,183 feet offshore.  The Unit No. 3 outfall extends from 3,558 feet to 6,020 feet offshore.  The Ocean Plan dilution factor assigned to both Unit No. 2 and 3 outfalls is 10.0.

10.	Issuance of this addendum is exempt from the requirement for preparation of environmental documents under the California Environmental Quality Act (Public Resources Code, Division 13, Chapter 3, Section 21000, et seq.) in accordance with Section 13389 of the California Water Code.

11.	The SDRWQCB has notified SCE and all known interested parties of its intent to modify Order No. 99-47 and 99-48.

12.	The SDRWQCB has, at a public meeting, heard and considered all comments pertaining to this addendum to Order Nos. 99-47 and 99-48.

IT IS HEREBY ORDERED that Order Nos. 99-47 and 99-48 be revised as follows:

1.	Add the following to the Findings Section of Order Nos. 99-47 and 99-48:

80.	By letter dated and received December 10, 1999, SCE requested permission to discharge wastes generated at Unit No. 1 through the Unit No. 2 and/or No. 3 outfall.  Additional discharge limitations and monitoring requirements have been added accordingly.  SCE is allowed to discharge all regulated waste sources noted in Finding 10 of Order 2000-04 through the Unit No. 2 and/or No. 3 outfall, subject to the limitations contained within this order.

2.	Add the following to Section B, Discharge Limitations of Order Nos. 99-47 and 99-48:

26.	Discharge of all SONGS Unit 1 Low Volume wastes, including radwaste, steam generator draindown, and the oil removal system to the once-through cooling water flow containing pollutants in excess of the following effluent limitations is prohibited:

| Parameter | Units | Monthly Average | Daily Maximum | Instant Maximum |
| --- | --- | --- | --- | --- |
| Total Suspended Solids | mg/l | 30.0 | 100.0 | 100.0 |
| Grease and Oil | mg/l | 15.0 | 20.0 | 20.0 |

27.	Discharges of any Metal Cleaning wastes generated by SONGS Unit No. 1 containing pollutants in excess of the following limitations is prohibited:

| Parameter | Units | Monthly Average | Daily Maximum | Instant Maximum |
| --- | --- | --- | --- | --- |
| Total Suspended Solids | mg/l | 30.0 | 100.0 | 100.0 |
| Grease and Oil | mg/l | 15.0 | 20.0 | 20.0 |
| Copper, total | mg/l | 1.0 | 1.0 | 1.0 |
| Iron, total | mg/l | 1.0 | 1.0 | 1.0 |

3.	Replace Discharge Specification B.1, to Order Nos. 99-47 and 99-48 with the following:

1.	The combined discharge through the outfall to the Pacific Ocean containing pollutants in excess of the following effluent limitations is prohibited.1/

| Parameter | Units | Instantaneous Maximum6/ |
| --- | --- | --- |
| Arsenic | ug/l | 850 |
| Cadmium | ug/l | 110 |
| Chromium (Hexavalent)7/ | ug/l | 220 |
| Copper | ug/l | 310 |
| Lead | ug/l | 220 |
| Mercury | ug/l | 4.4 |
| Nickel | ug/l | 550 |
| Selenium | ug/l | 1700 |
| Silver | ug/l | 75 |
| Zinc | ug/l | 2100 |

| Parameter | Units | Monthly Average10/ | Weekly Average11/ | Daily Maximum5/ | Maximum at any time |
| --- | --- | --- | --- | --- | --- |
| Total Chlorine Residual8/ | ug/l | 22 | 88 | 200 | -- |
| Acute Toxicity12/ | TUa | 1.5 | 2.0 | -- | 2.5 |
| Chronic Toxicity12/ | TUc | -- | -- | 10 | -- |

Note:  ug/l = micrograms per liter

4.	Add the following to section B, Discharge Specifications of Order Nos. 99-47 and 99-48:

- The combined discharge from all in-plant waste sources, sampled as specified in section E of the Monitoring and Reporting Program of this Order, to the once-through cooling water flow containing pollutants in excess of the following effluent limitations is prohibited:

(These are maximum limitations that are calculated using the procedure outlined on page 13 of the Ocean Plan using an initial dilution value of 10.0 and a maximum flowrate of 1286.9 MGD.  For compliance purposes, the actual limit shall be determined by the following formula:

Lf = (Qa/Qm) Lt

Lf = final limit used for compliance determination

Qa = combined discharge flowrate at the time of

sampling

Qm = 1300 MGD

Lt = any limit in the following tables with units

"lb/Day")

| Parameter | Units | 6-Month Median | Daily Maximum |
| --- | --- | --- | --- |
| Arsenic | lb/Day | 620 | 3,500 |
| Cadmium | lb/Day | 120 | 480 |
| Chromium (Hexavalent)7/ | lb/Day | 240 | 950 |
| Copper | lb/Day | 130 | 1,200 |
| Lead | lb/Day | 240 | 950 |
| Mercury | lb/Day | 5 | 19 |
| Nickel | lb/Day | 590 | 2,400 |
| Selenium | lb/Day | 1,800 | 7,100 |
| Silver | lb/Day | 70 | 320 |
| Zinc | lb/Day | 1,500 | 8,600 |
| Cyanide | lb/Day | 120 | 480 |
| Ammonia (as N) | lb/Day | 55,000 | 270,000 |
| Phenolic Compounds (non- Chlorinated) | lb/Day | 3,100 | 14,000 |
| Chlorinated Phenolics | lb/Day | 120 | 500 |
| Endosulfan | lb/Day | 1.1 | 2.1 |
| Endrin | lb/Day | 0.24 | 0.47 |
| HCH9/ | lb/Day | 0.47 | 0.94 |

| Parameter | Units | 30-day Average |
| --- | --- | --- |
| Acrolein | lb/Day | 26,000 |
| Antimony | lb/Day | 140,000 |
| Bis(2-chloroethoxy) methane | lb/Day | 520 |
| Bis(2-chloroisopropyl) ether | lb/Day | 140,000 |
| Chlorobenzene | lb/Day | 67,000 |
| Chromium (III) | lb/Day | 22,000,000 |
| Di-n-butyl phthalate | lb/Day | 410,000 |
| Dichlorobenzenes | lb/Day | 600,000 |
| 1,1-dichloroethylene | lb/Day | 840,000 |
| Diethyl phthalate | lb/Day | 3,900,000 |
| Dimethyl phthalate | lb/Day | 97,000,000 |
| 4,6-dinitro-2-methylphenol | lb/Day | 26,000 |
| 2,4-dinitrophenol | lb/Day | 470 |
| Ethylbenzene | lb/Day | 480,000 |
| Fluoranthene | lb/Day | 1,800 |
| Hexachlorocyclopentadiene | lb/Day | 6,800 |
| Isophorone | lb/Day | 18,000,000 |
| Nitrobenzene | lb/Day | 580 |
| Thallium | lb/Day | 1,700 |
| Toluene | lb/Day | 10,000,000 |
| 1,1,2,2-tetrachloroethane | lb/Day | 140,000 |
| Tributyltin | lb/Day | 0.17 |
| 1,1,1-trichloroethane | lb/Day | 64,000,000 |
| 1,1,2-trichloroethane | lb/Day | 5,100,000 |
| Acrylonitrile | lb/Day | 12 |
| Aldrin | lb/Day | 0.0026 |
| Benzene | lb/Day | 700 |
| Benzidine | lb/Day | 0.0081 |
| Beryllium | lb/Day | 3.9 |
| Bis (2-chloroethyl) ether | lb/Day | 5.3 |
| Bis (2-ethylhexyl) phthalate | lb/Day | 410 |
| Carbon Tetrachloride | lb/Day | 110 |
| Chlordane | lb/Day | 0.0027 |
| Chloroform | lb/Day | 15,000 |
| DDT | lb/Day | 0.02 |
| 1,4-dichlorobenzene | lb/Day | 2,100 |
| 3,3-dichlorobenzidine | lb/Day | 0.96 |
| 1,2-dichloroethane | lb/Day | 15,000 |
| Dichloromethane | lb/Day | 53,000 |
| 1,3-dichloropropene | lb/Day | 1,100 |
| Dieldrin | lb/Day | 0.0047 |
| 2,4-dinitrotoluene | lb/Day | 310 |
| 1,2-diphenylhydrazine | lb/Day | 19 |
| Halomethanes | lb/Day | 15,000 |
| Heptachlor | lb/Day | 0.085 |
| Hexachlorobenzene | lb/Day | 0.025 |
| Hexachlorobutadiene | lb/Day | 1,700 |
| Hexachloroethane | lb/Day | 300 |
| N-nitrosodimethylamine | lb/Day | 860 |
| N-nitrosodiphenylamine | lb/Day | 300 |
| PAHs | lb/Day | 1.0 |
| PCBs | lb/Day | 0.0021 |
| TCDD equivalents | lb/Day | 0.00000046 |
| Tetrachloroethylene | lb/Day | 12,000 |
| Toxaphene | lb/Day | 0.025 |
| Trichloroethylene | lb/Day | 3,200 |
| 2,4,6-trichlorophenol | lb/Day | 34 |
| Vinyl Chloride | lb/Day | 4,300 |

5.	Replace Section D, Combined Discharge Monitoring, of the Monitoring and Reporting Programs for Order Nos. 99-47 and 99-48 with the following:

D.	Combined Discharge3/ Monitoring

Samples of the combined discharge shall be collected in accordance with the following criteria:

| Parameter | Units | Type of Sample | Minimum Frequency |
| --- | --- | --- | --- |
| Flow | MGD | -- | Continuous |
| Turbidity | NTU | Grab | Monthly |
| Acute Toxicity7/ | TUa | Composite | Quarterly |
| Chronic Toxicity7/ | TUc | Composite | Semiannually |
| Chronic Toxicity (metal cleaning)12/ | TUc | Composite | 12/ |
| Temperature9/ | F | -- | Continuous |
| PH | PH units | Grab | Monthly |
| Total Chlorine Residual5/ | ug/L | Grab | Monthly |
| Hydrazine | ug/L | Grab | Monthly |
| Arsenic | ug/L | Grab | Semiannually |
| Cadmium | ug/L | Grab | Semiannually |
| Chromium (Hexavalent)4/ | ug/L | Grab | Semiannually |
| Copper | ug/L | Grab | Semiannually |
| Lead | ug/L | Grab | Semiannually |
| Mercury | ug/L | Grab | Semiannually |
| Nickel | ug/L | Grab | Semiannually |
| Selenium | ug/L | Grab | Semiannually |
| Silver | ug/L | Grab | Semiannually |
| Zinc | ug/L | Grab | Semiannually |

6.	Endnote 2 of the Monitoring and Reporting Programs for Order Nos. 99-47 and 99-48 is deleted.

7.	Replace Section E, In-Plant Waste Streams Monitoring, of the Monitoring and Reporting Programs for Order Nos. 99-47 and 99-48, with the following:

E.	IN-PLANT WASTE STREAMS MONITORING

The following shall constitute the in-plant waste stream monitoring program.  The reported values shall result from individual grab samples of in-plant waste streams that are collected and composited on a flow-weighted basis.  Measurements or estimates of flows of individual in-plant waste streams used as a basis for compositing shall be reported as well as the names of all waste streams sampled.  The final sample should include as many wastes as possible.  The highest priority waste streams are metal cleaning wastes, radwaste, full flow condensate polishing demineralizer regenerants and high flow make-up demineralizer regenerants.  The flowrate used to determine the proportion of each waste stream in the combined sample shall be the yearly average.

The final composite sample shall be derived from all of the following wastestreams:

Unit 2: thermophilic digester, condenser hotwell overboard, steam generator blowdown, blowdown processing system demineralizer regenerants, full flow condensate polishing demineralizer regenerants, makeup demineralizer regenerants, radwaste system, Unit 2 oil/water separator, intake structure sump, metal cleaning waste, seawater pumps bearing flush water, storm drains, and domestic wastewater treatment plants.  If any of the following wastes generated at Unit No. 1 are discharged through the Unit No. 2 outfall during the year prior to sampling, they should be included in the composite sample: metal cleaning wastes, radwaste, steam generator draindown, and oil removal system.

Unit 3: thermophilic digester, condenser hotwell overboard, steam generator blowdown, blowdown processing system demineralizer regenerants, full flow condensate polishing demineralizer regenerants, makeup demineralizer regenerants, radwaste system, oil/water flocculator, intake structure sump, metal cleaning waste, seawater pumps bearing flush water, storm drains, and domestic wastewater treatment plants. If any of the following wastes generated at Unit No. 1 are discharged through the Unit No. 3 outfall during the year prior to sampling, they should be included in the composite sample: metal cleaning wastes, radwaste, steam generator draindown, and oil removal system.

| Parameter | Units | Minimum Frequency of Analysis | Reporting Frequency |
| --- | --- | --- | --- |
| PH | pH units | Annual | Annual |
| Arsenic | lb/Day | Annual | Annual |
| Cadmium | lb/Day | Annual | Annual |
| Chromium (Hexavalent)4/ | lb/Day | Annual | Annual |
| Copper | lb/Day | Annual | Annual |
| Lead | lb/Day | Annual | Annual |
| Mercury | lb/Day | Annual | Annual |
| Nickel | lb/Day | Annual | Annual |
| Selenium | lb/Day | Annual | Annual |
| Silver | lb/Day | Annual | Annual |
| Zinc | lb/Day | Annual | Annual |
| Cyanide | lb/Day | Annual | Annual |
| Ammonia (expressed as nitrogen) | lb/Day | Annual | Annual |
| Phenolic Compounds (non-chlorinated) | lb/Day | Annual | Annual |
| Chlorinated Phenolics | lb/Day | Annual | Annual |
| Endosulfan | lb/Day | Annual | Annual |
| Endrin | lb/Day | Annual | Annual |
| HCH6/ | lb/Day | Annual | Annual |
| Acrolein | lb/Day | Annual | Annual |
| Antimony | lb/Day | Annual | Annual |
| Bis(2-chloroethoxy) methane | lb/Day | Annual | Annual |
| Bis (2-chloroisopropyl) ether | lb/Day | Annual | Annual |
| Chlorobenzene | lb/Day | Annual | Annual |
| Chromium (III) | lb/Day | Annual | Annual |
| Di-n-butyl phthalate | lb/Day | Annual | Annual |
| Dichlorobenzenes | lb/Day | Annual | Annual |
| 1,1-dichloroethylene | lb/Day | Annual | Annual |
| Diethyl phthalate | lb/Day | Annual | Annual |
| Dimethyl phthalate | lb/Day | Annual | Annual |
| 4,6-dinitro-2-methylphenol | lb/Day | Annual | Annual |
| 2,4-dinitrophenol | lb/Day | Annual | Annual |
| Ethylbenzene | lb/Day | Annual | Annual |
| Fluoranthene | lb/Day | Annual | Annual |
| Hexachlorocyclopentadiene | lb/Day | Annual | Annual |
| Isophorone | lb/Day | Annual | Annual |
| Nitrobenzene | lb/Day | Annual | Annual |
| Thallium | lb/Day | Annual | Annual |
| Toluene | lb/Day | Annual | Annual |
| 1,1,2,2-tetrachloroethane | lb/Day | Annual | Annual |
| Tributyltin | lb/Day | Annual | Annual |
| 1,1,1-trichloroethane | lb/Day | Annual | Annual |
| 1,1,2-trichloroethane | lb/Day | Annual | Annual |
| Acrylonitrile | lb/Day | Annual | Annual |
| Aldrin | lb/Day | Annual | Annual |
| Benzene | lb/Day | Annual | Annual |
| Benzidine | lb/Day | Annual | Annual |
| Beryllium | lb/Day | Annual | Annual |
| Bis (2-chloroethyl) ether | lb/Day | Annual | Annual |
| Bis (2-ethylhexyl) phthalate | lb/Day | Annual | Annual |
| Carbon tetrachloride | lb/Day | Annual | Annual |
| Chlordane | lb/Day | Annual | Annual |
| Chloroform | lb/Day | Annual | Annual |
| DDT | lb/Day | Annual | Annual |
| 1,4-dichlorobenzene | lb/Day | Annual | Annual |
| 3,3-dichlorobenzidine | lb/Day | Annual | Annual |
| 1,2-dichloroethane | lb/Day | Annual | Annual |
| Dichloromethane | lb/Day | Annual | Annual |
| 1,3-dichloropropene | lb/Day | Annual | Annual |
| Dieldrin | lb/Day | Annual | Annual |
| 2,4-dinitrotoluene | lb/Day | Annual | Annual |
| 1,2-diphenylhydrazine | lb/Day | Annual | Annual |
| Halomethanes | lb/Day | Annual | Annual |
| Heptachlor | lb/Day | Annual | Annual |
| Hexachlorobenzene | lb/Day | Annual | Annual |
| Hexachlorobutadiene | lb/Day | Annual | Annual |
| Hexachloroethane | lb/Day | Annual | Annual |
| N-nitrosodimethylamine | lb/Day | Annual | Annual |
| N-nitrosodiphenylamine | lb/Day | Annual | Annual |
| PAHs | lb/Day | Annual | Annual |
| PCBs | lb/Day | Annual | Annual |
| TCDD equivalents | lb/Day | Annual | Annual |
| Tetrachloroethylene | lb/Day | Annual | Annual |
| Toxaphene | lb/Day | Annual | Annual |
| Trichloroethylene | lb/Day | Annual | Annual |
| 2,4,6-trichlorophenol | lb/Day | Annual | Annual |
| Vinyl Chloride | lb/Day | Annual | Annual |

8.	Add the following to the Endnotes section of the Monitoring and Reporting Programs of Order Nos. 99-47 and 99-48:

12.	An additional toxicity test shall be performed during the discharge of metal cleaning wastes.  Sampling shall occur at the combined discharge.

9.	Section J, Receiving Water Monitoring, part 6 and 7 of the Monitoring and Reporting programs of Order Nos. 99-47 and 99-48 are revised as follows:

A.	Add additional control stations H22S, J22S, and M22S and remove stations F24S, F26S, and F20S for temperature and transmissometer profiles (Attachment 1).

- Provision 10 of Order Nos. 99-47 and 99-48 is deleted.

11.	Replace Monitoring Provision 22 of the Monitoring and Reporting Programs for Order Nos. 99-47 and 99-48 with the following:

22.  Toxicity Provisions

a)	Implementation of the Acute and Chronic Limits

If the results of an acute or chronic toxicity test exceeds the limits specified in this order, the discharger shall:

- Take all reasonable measures necessary to immediately minimize toxicity; and

2)	Increase the frequency of the toxicity test(s) that violated the effluent limitation to at least two times per month until the results of at least three consecutive toxicity tests meet the required standard.  Resampling should occur under conditions that mimic the conditions of the initial non-compliant toxicity test.

If the Executive Officer determines that toxicity testing shows a consistent violation of the limits specified in this order, the discharger shall conduct a TRE which includes all reasonable steps to identify the source of toxicity.  Once the source of toxicity is identified, upon the Executive Officer's request, the discharger shall take all reasonable steps to reduce the toxicity to meet the toxicity limitations contained in this Order.

Within fourteen days of completion of the TRE, the discharger shall submit the results of the TRE, including a summary of the findings, data generated, a list of corrective actions necessary to achieve consistent compliance with this Order and prevent future violations, and a time schedule for implementation of such corrective actions.  The corrective actions and time schedule shall be modified at the discretion of the Executive Officer.

The EPA acute and chronic manuals EPA/600/6-91/005F (Phase I), EPA/600/R-92/080 (Phase II), and EPA/600/R-92/081 (Phase III) and EPA/600/2-88/070, (TRE protocol for industrials) are excellent resource documents that may be helpful to the discharger.

b)	Toxicity Reopener

This permit may be modified in accordance with the requirements set forth at 40 CFR Part 122 and 124, to include appropriate conditions or limits to address demonstrated effluent toxicity based on newly available information, or to implement any EPA-approved new state water quality standards applicable to effluent toxicity.

12.	Replace Section L of the Monitoring and Reporting Programs of Order Nos. 99-47 and 99-48 with the following:

- MONITORING REPORT SCHEDULE

Monitoring reports shall be submitted to the Executive Officer according to the dates in the following schedule:

Monitoring Frequency				Report Due

Monthly	First Day of the second month after the month of sampling

Quarterly	First day of the second month after the quarter ends: May 1st, August 1st, November 1st, and February 1st.

Semiannual	First day of the second month after the 6-month period: August 1st and February 1st.

Annual						February 1st.

- Add a section M to the Monitoring and Reporting Program for Order Nos. 99-47 and 99-48 to read as follows:

- BACTERIAL MONITORING PROGRAM

The following program shall measure compliance with Part D, Receiving Water Limitations, Section 2, part a, Bacterial Characteristics.  Results shall be reported monthly.  All sampling shall be performed according to procedures specified in Appendix II of the California Ocean Plan 1997.  If any data point in the monthly report indicates a total coliform density greater than 10,000 organisms/100ml, a fecal coliform density greater than 400 organisms/100ml, or an enteroccus density greater than 104 organisms/100ml then a copy of that report shall also be sent to:

San Diego Department of Environmental Health

Recreational Water Quality Program

P.O. Box 129261

San Diego, CA 92112-9261

Fax: (619)338-2174

Phone (Clay Clifton): (619)338-2386

- Receiving Water Stations

Monthly grab sampling shall occur at two locations shown in Attachment 2.  The two locations shall be located 500 feet shoreward of the Unit 1 Outfall.  Station one shall be located 500 feet upcoast and the station two shall be located 500 feet downcoast.  Samples shall be taken from surface, mid-depth, and bottom and be analyzed for total coliform density, fecal coliform density, and enterococcus density.  Results shall be reported in units of number of organisms per/100ml.

- Shore Stations

Monthly grab sampling shall occur in the surfzone at two locations.  Samples shall be analyzed for total coliform density, fecal coliform density, and enterococcus density.  Results shall be reported in units of number of organisms per/100ml.

- Station 1 shall be located at the San Onofre Surfing Beach located several hundred yards upcoast of the power plant.

- Station 2 shall be located in the San Onofre Bluffs area located downcoast of the power plant.  Sampling shall occur at the beach access point at the end of Trail 6.

From April 1 to October 31 of every year, Station 1 shall be monitored weekly.  The results of this monitoring shall be transmitted as soon as possible after obtaining the sample results to the San Diego Department of Environmental Health.  The results shall also be summarized in the standard monthly report sent to the Regional Board.

I, John H. Robertus, Executive Officer, do hereby certify the foregoing is a full, true, and correct copy of an Addendum adopted by the California Regional Water Quality Control Board, San Diego Region, on August 30, 2000.  This Addendum shall take effect November 30, 2000.

__________________________

JOHN H. ROBERTUS

Executive Officer