CALIFORNIA REGIONAL WATER QUALITY CONTROL BOARD

SAN DIEGO REGION

NPDES NO. CA0108073

MONITORING AND REPORTING PROGRAM NO. 99-47

FOR

SOUTHERN CALIFORNIA EDISON COMPANY

SAN ONOFRE NUCLEAR GENERATING STATION, UNIT 2

SAN DIEGO COUNTY

A.	MONITORING PROVISIONS

1.	Monitoring results shall be reported at intervals specified 	elsewhere in this monitoring and reporting program.

2.	This monitoring plan may be modified to incorporate changes in frequency or types of analysis to be consistent with the Regional Monitoring Program which is currently under development.

3.	Samples and measurements taken as required herein shall be representative of the volume and nature of the monitored discharge.  All samples shall be taken at the monitoring points specified in this Order and, unless otherwise specified, before the effluent joins or is diluted by any other waste stream, body of water, or substance.  Monitoring points shall not be changed without notification to and the approval of the Executive Officer.

4. 	Appropriate flow measurement devices and/or methods for calculating flowrates shall be consistent with accepted scientific practices to ensure the accuracy and reliability of measurements of the volume of monitored discharges.  Any flow measuring device used shall be installed, calibrated and maintained to ensure that the accuracy of the measurements are consistent with the accepted capability of that type of device.  Devices selected shall be capable of measuring flows with a maximum deviation of less than +5 percent from true discharge rates throughout the range of expected discharge volumes.  Guidance in selection, installation, calibration and operation of acceptable flow measurement devices can be obtained from the following references:

a.	"Guide to Methods and Standard for the Measurement of Water Flow," U.S. Department of Commerce, National Bureau of Standards, NBS Special Publication 421, May l975, 97 pp. (Available from the U.S. Government Printing Office, Washington, D.C. 20402.  Order by SD Catalog No. C13.10:421.)

b.	"Water Measurement Manual," U.S. Department of Interior, Bureau of Reclamation, Second Edition, Revised Reprint, l974, 327 pp. (Available from the U.S. Government Printing Office, Washington D. C. 20402.  Order by Catalog No. 127, 19/2:W29/2, Stock No. S/N 24003-0027.)

c.	"Flow Measurement in Open Channels and Closed Conduits," U.S. Department of Commerce, National Bureau of Standards, NBS Special Publication 484, October 1977, 982 pp. (Available in paper copy of microfiche from National Technical Information Service (NTIS) Springfield, VA 22151.  Order by NTIS No. PB-273-535/5ST.)

d.	"NPDES Compliance Sampling Manual," U.S. Environmental Protection Agency, Office of Water Enforcement.  Publication MCD-51, 1977, 140 pp.  (Available from the General Services Administration (8FFS), Centralized Mailing Lists Services, Building 41, Denver Federal Center, Denver, CO 80225).

5.	Monitoring must be conducted according to United States Environmental Protected Agency test procedures approved under Title 40, Code of Federal Regulations (CFR), Part 136, "Guidelines Establishing Test Procedures for Analysis of Pollutants Under the Clean Water Act" as amended, unless otherwise specified in 40 CFR part 503, unless other test procedures have been specified in this Order.

6.	All analyses shall be performed in a laboratory certified to perform such analyses by the California Department of Health Service or a laboratory approved by the Executive Officer.

7.	If the discharger monitors any pollutants more frequently than required by this Order, using test procedures approved under 40 (CFR), Part 136, or, in the case of sludge use and disposal, approved under 40 CFR part 136 unless otherwise specified in 40 CFR part 503, or as specified in this Order, the results of this monitoring shall be included in the calculation and reporting of the data submitted in the discharger's monitoring report.  The increased frequency of monitoring shall also be reported.

8.	The discharger shall retain records of all monitoring information, including all calibration and maintenance records and all original strip chart recordings for continuous monitoring instrumentation, copies of all reports required by this Order, and records of all data used to complete the application for this Order.  Records shall be maintained for a minimum of five years from the date of the sample, measurement, report, or application.  This period may be extended during the course of any unresolved litigation regarding this discharge of when requested by the Regional Board Executive Officer of the United States Environmental Protection Agency.

9.	Records of monitoring information shall include:

a.	The date, exact place, and time of sampling or measurements;

b.	The individual(s) who performed the sampling or measurements;

c.	The date(s) analyses were performed;

d.	The individual(s) who performed analyses;

e.	The analytical techniques of method used; and

f.	The results of such analyses.

10.	Calculations for all limitations which require averaging of measurements shall utilize an arithmetic mean unless otherwise specified by the Executive Officer or in this Order.

11.	All monitoring instruments and devices used by the discharger to fulfill the prescribed monitoring program shall be properly maintained and calibrated as necessary to ensure their continued accuracy.  All flow measurement devices shall be calibrated at least once per year, or more frequently, to ensure continued accuracy of the devices.

12.	The discharger shall have, and implement, an acceptable written quality assurance (QA) plan for laboratory analyses. Duplicate chemical analyses must be conducted on a minimum of ten percent of the samples or at least one sample per month, whichever is greater.  A similar frequency shall be maintained for analyzing spiked samples.  The discharger should have a success rate equal to or greater than 80 percent.

13.	The discharger shall report all instances of noncompliance not reported under Reporting Requirement F.5 of this Order at the time monitoring reports are submitted.  The reports shall contain the information listed in Reporting Requirement F.5.

14.	The monitoring reports shall be signed by an authorized person as required by Reporting Requirement No. F.10.

15.	A composite sample is defined as a combination of 24 aliquots of at least 100 milliliters each, collected hourly over a 24-hour period.  Each individual aliquot must consist of 4 samples taken at 15 minute intervals.  The composite must be flow proportional; either the time interval between each aliquot or the volume of each aliquot must be proportional to either the stream flow at the time of sampling or the total stream flow since the collection of the previous aliquot.  Aliquots may be collected manually or automatically.

16.	A grab sample is an individual sample of at least 100 milliliters collected at a randomly selected time over a period not exceeding 15 minutes.

17.	Reports of marine monitoring surveys conducted to meet receiving water monitoring requirements of the "Monitoring and Reporting Program" shall include, as a minimum, the following information:

a.	A description of climatic and receiving water characteristics at the time of sampling (weather observations, floating debris, discoloration, wind speed and direction swell or wave action, time of sampling, tide height, etc.).

b.	A description of sampling stations, including difference unique to each station (e.g., station location, sediment grain size, distribution of bottom sediments, rocks, shell litter, calcareous worm tubes, etc.).

c.	A description of the sample collection and preservation procedures used in the survey.

d.	A description of the specific method used for laboratory analysis.

e.	An in-depth discussion of the results of the survey.  The discussion shall compare data from the reference station(s) with data from the stations located in the area of the discharge.  All tabulations and computations shall be explained.

18.	For all bacterial analyses, sample dilutions should be performed so the range of values extends from 2 to 16,000.  The detection method used for each analysis shall be reported with the results of the analysis.

19.	Detection methods used for coliform analyses (total and fecal) shall be those presented in the most recent edition of Standard Methods for the Examination of Water and Wastewater or any improved method determined by the Regional Board, and approved by EPA, to be appropriate.

Detection methods used for enterococcus shall be those presented in EPA publication EPA 600/4-85/076, Test Methods for Escherichia coli and Enterococci in Water By Membrane Filter Procedure or any improved method determined by the  Executive Officer to be appropriate.

20.	Acute Toxicity Testing

The presence of acute toxicity shall be determined as specified in Methods for Measuring the Acute Toxicity of Effluents to Freshwater and Marine Organisms (EPA 600/4-90-027F, August, 1993 or subsequent editions).   The permittee shall conduct quarterly toxicity tests on a composite sample of the effluent.  Samples shall be taken at the NPDES sampling location of the combined discharge.  There is no mixing zone allowance for acute toxicity.  The permittee shall conduct quarterly 96 hour static-renewal tests using, Menidia beryllina.  The effluent concentrations will be 100%, 75%, 50%, 25%, and 12.5% and a control.  Note:  When the State Water Resources Control Board approves the use of topsmelt, Atherinops affinis this species will replace the use of Menidia beryllina.  The effluent tests must be conducted with concurrent reference toxicant tests.  Both the reference toxicant and the effluent test must meet all test acceptability criteria as specified in the acute manual.   If the test acceptability criteria is not achieved, then the permittee must re-sample and re-test within 14 days.

The test results must be reported to the Regional Board according to chapter 12 of Methods for Measuring the Acute Toxicity of Effluents and Receiving Waters to Freshwater and Marine Organisms.  Section 12.2, section 12.3.2, and section 12.7.5 may be omitted.

Compliance with acute toxicity will be expressed as TUa, which equals 100/NOAEC.  No Observable Adverse Effect Concentration (NOAEC) is the highest concentration at which survival is not significantly different from the control in a 96-hour renewal test.

21. 	Chronic Toxicity Testing

The permittee shall conduct semiannual toxicity tests on 24-hour composite effluent samples.  Testing shall be performed using methods outlined in "Chapman, G.A., D.L. Denton, and J.M. Lazorchak. 1995.  Short-term methods for estimating the chronic toxicity of effluents and receiving waters to west coast marine and estuarine organisms" or "SWRCB 1996.  Procedures Manual for Conducting Toxicity Tests Developed by the Marine Bioassay Project.  96-1WQ."

The samples shall be taken during a period when low volume wastes are being discharged. Samples shall be taken at the NPDES sampling location of the combined discharge.  At the time of the first toxicity test immediately following adoption of this permit, the permittee shall conduct toxicity tests with an invertebrate, Haliotis rufescens, a plant Macrocystis pyrifera, and a vertebrate Atherinops Affinis.  After this screening period, monitoring will be conducted on the most sensitive species.  Every two years the permittee shall re-screen to determine the most sensitive species.  This screening shall be performed on a different month than previous species screenings.  The most sensitive species shall then be used.

At least five concentrations of effluent (one concentration must bracket the initial dilution of 10% effluent) plus a control, shall be tested.  A minimum of four replicates is required per concentration.  The effluent tests must be conducted with concurrent reference toxicant tests. Both the reference toxicant and effluent test must meet all test acceptability criteria as specified in the chronic manuals. If the test acceptability criteria is not achieved, then the permittee must re-sample and re-test within 14 days.

The summary report submitted to the Regional Board must follow the guidelines specified in Chapter 10 of Short-Term Methods for Estimating the Chronic Toxicity of Effluents and Receiving Waters to West Coast Marine and Estuarine Organisms.  Section 10.2 and section 10.3.2 of that chapter is not required.

Compliance shall be determined from TUc, which equals 100/NOEC.  NOEC (No Observed Effect Concentration) is the highest concentration of toxicant, in terms of percent effluent, to which the test organisms are exposed that causes no observable adverse effect.  The chronic toxicity limitation is:  1) a monthly median expressed as 10 TUc or 2) any one test that demonstrates a 50% toxic effect.

22.	Toxicity Provisions

a)	Alternative Protocols

The permittee may propose to the Regional Board Executive Officer in writing that compliance with the acute toxicity limit be based on the mortality data from the chronic tests data.

b)	Implementation of the Acute and Chronic Limits

The permittee must maintain an up to date Toxicity Reduction Evaluation (TRE) workplan.

Whenever the acute or chronic toxicity effluent limitation as defined has been exceeded, the Permittee shall, within (15) days:

(i)	In accordance with EPA manuals EPA/600/2-88/070, (TRE protocol for industrials) or any subsequent revisions, the discharger shall conduct a toxicity reduction evaluation (TRE) where appropriate; and

(ii)	In accordance with EPA acute and chronic TIE manuals EPA/600/6-91/003F (Phase I), EPA/600/R-92/080 (Phase II), EPA/600/R-92/081 (Phase III), and the Phase I draft manual for marine testing, the discharger shall conduct a toxicity identification reduction (TIE) within (15) days of the exceedance to identify the cause(s) of the toxicity;

(iii) Notify the State agency within (5) days of

becoming aware of the exceedance:

(1)	times and dates when the limitation was exceeded;

(2)	the finding of the TIE or other investigation to identify the cause(s) of the toxicity;

(3)	the actions the permittee has taken or will take to mitigate the impact of the discharge, to correct the noncompliance and prevent the recurrence of toxicity; and

(4)	where corrective actions including TRE or TIE, have not been completed, expeditious schedule under which the corrective actions will be implemented.

d)  Toxicity Reopener

This permit may be modified in accordance with the requirements set forth at 40 CFR Part 122 and 124, to include appropriate conditions or limits to address demonstrated effluent toxicity based on newly available information, or to implement any EPA-approved new state water quality standards applicable to effluent toxicity.

23.	The monitoring program for a discharger with discharge requirements shall:

a)	Determine compliance with the terms and conditions of Order No. 99-47.

b)	Determine that the applicable State and federal water quality standards are met.

24.	Revisions of the monitoring program by the Regional Board staff are appropriate to ensure that the discharger is in compliance with requirements and provisions contained in this order.  Revisions may be made by the Executive Officer at any time during the term of this Order, and may include a reduction or increase in the number of parameters to be monitored, the frequency of monitoring, or the number and size of samples collected.

B.	FISH ENTRAINMENT MONITORING

1.	Monitoring

During heat treatments and for at least one continuous 24-hour period per quarter during normal operation, the following shall be obtained:

(a)	Total weight and number of each species of fish removed from the traveling bar racks and screens.

(b)	Standard length and sex of select species in a representative sample1/ removed from the traveling bar racks and screens.

2.	Reporting

(a)	A report containing detailed analyses of the previous year's fish entrainment monitoring data shall be submitted by July 30 of each year.  The report shall contain a narrative and graphical summary of all historical data with the goal of displaying long term trends.

C.	COOLING WATER INTAKE MONITORING

Samples of the cooling water intake shall be collected in accordance with the following criteria:

| Parameter | Units | Sample Type | Minimum Frequency of Analysis |
| --- | --- | --- | --- |
| Flow | MGD | -- | Continuous |
| Turbidity | NTU | Grab | Monthly |
| Temperature9/ | F | -- | Continuous |
| PH | pH units | Grab | Monthly |

D.	COMBINED DISCHARGE3/ MONITORING

Samples of the combined discharge shall be collected in accordance with the following criteria:

| Parameter | Units | Type of Sample2/ | Minimum Frequency |
| --- | --- | --- | --- |
| Flow | MGD | -- | Continuous |
| Turbidity | NTU | Grab | Monthly |
| Acute Toxicity7/ | TUa | Composite | Quarterly |
| Chronic Toxicity7/ | TUc | Composite | Semiannually |
| Temperature9/ | F | -- | Continuous |
| PH | pH units | Grab | Monthly |
| Total Chlorine Residual5/ | Ug/L | Grab | Monthly |
| Hydrazine | ug/l | Grab | Monthly |
| Arsenic | ug/L | Composite | Semiannually |
| Cadmium | ug/L | Composite | Semiannually |
| Chromium (Hexavalent)4/ | ug/L | Composite | Semiannually |
| Copper | ug/L | Composite | Semiannually |
| Lead | ug/L | Composite | Semiannually |
| Mercury | ug/L | Composite | Semiannually |
| Nickel | ug/L | Composite | Semiannually |
| Selenium | ug/L | Composite | Semiannually |
| Silver | ug/L | Composite | Semiannually |
| Zinc | ug/L | Composite | Semiannually |
| Cyanide | ug/L | Composite | Semiannually |
| Ammonia (expressed as nitrogen) | ug/L | Composite | Semiannually |
| Phenolic Compounds (non-chlorinated) | ug/L | Composite | Semiannually |
| Chlorinated Phenolics | ug/L | Composite | Semiannually |
| Endosulfan | ug/L | Composite | Semiannually |
| Endrin | ug/L | Composite | Semiannually |
| HCH6/ | ug/L | Composite | Semiannually |
| Acrolein | ug/L | Composite | Annually |
| Antimony | ug/L | Composite | Annually |
| Bis(2-chloroethoxy) methane | ug/L | Composite | Annually |
| Bis(2-chloroisopropyl) ether | ug/L | Composite | Annually |
| Chlorobenzene | ug/L | Composite | Annually |
| Chromium (III) | ug/L | Composite | Annually |
| di-n-butyl phthalate | ug/L | Composite | Annually |
| Dichlorobenzenes | ug/L | Composite | Annually |
| 1,1-dichloroethylene | ug/L | Composite | Annually |
| Diethyl phthalate | ug/L | Composite | Annually |
| Dimethyl phthalate | ug/L | Composite | Annually |
| 4,6-dinitro-2-methylphenol | ug/L | Composite | Annually |
| 2,4-dinitrophenol | ug/L | Composite | Annually |
| Ethylbenzene | ug/L | Composite | Annually |
| Fluoranthene | ug/L | Composite | Annually |
| Hexachlorocyclopentadiene | ug/L | Composite | Annually |
| Isophorone | ug/L | Composite | Annually |
| Nitrobenzene | ug/L | Composite | Annually |
| Thallium | ug/L | Composite | Annually |
| Toluene | ug/L | Composite | Annually |
| 1,1,2,2-tetrachloroethane | ug/L | Composite | Annually |
| Tributyltin | ug/L | Composite | Annually |
| 1,1,1-trichloroethane | ug/L | Composite | Annually |
| 1,1,2-trichloroethane | ug/L | Composite | Annually |
| Acrylonitrile | ug/L | Composite | Annually |
| Aldrin | ug/L | Composite | Annually |
| Benzene | ug/L | Composite | Annually |
| Benzidine | ug/L | Composite | Annually |
| Beryllium | ug/L | Composite | Annually |
| Bis(2-chloroethyl) ether | ug/L | Composite | Annually |
| Bis(2-ethylhexyl) phthalate | ug/L | Composite | Annually |
| Carbon Tetrachloride | ug/L | Composite | Annually |
| Chlordane | ug/L | Composite | Annually |
| Chloroform | ug/L | Composite | Annually |
| DDT | ug/L | Composite | Annually |
| 1,4-dichlorobenzene | ug/L | Composite | Annually |
| 3,3-dichlorobenzidine | ug/L | Composite | Annually |
| 1,2-dichloroethane | ug/L | Composite | Annually |
| Dichloromethane | ug/L | Composite | Annually |
| 1,3-dichloropropene | ug/L | Composite | Annually |
| Dieldrin | ug/L | Composite | Annually |
| 2,4-dinitrotoluene | ug/L | Composite | Annually |
| 1,2-diphenylhydrazine | ug/L | Composite | Annually |
| Halomethanes | ug/L | Composite | Annually |
| Heptachlor | ug/L | Composite | Annually |
| Hexachlorobenzene | ug/L | Composite | Annually |
| Hexachlorobutadiene | ug/L | Composite | Annually |
| Hexachloroethane | ug/L | Composite | Annually |
| N-nitrosodimethylamine | ug/L | Composite | Annually |
| N-nitrododiphenylamine | ug/L | Composite | Annually |
| PAHs | ug/L | Composite | Annually |
| PCBs | ug/L | Composite | Annually |
| Tetrachlorethylene | ug/L | Composite | Annually |
| Toxaphene | ug/L | Composite | Annually |
| Trichloroethylene | ug/L | Composite | Annually |
| 2,4,6-trichlorophenol | ug/L | Composite | Annually |
| Vinyl chloride | Ug/L | Composite | Annually |

E.	IN-PLANT WASTE STREAMS10/ MONITORING

The following shall constitute the in-plant waste streams monitoring program.

| Parameter | Units | Type of Sample11/ | Minimum Frequency |
| --- | --- | --- | --- |
| Flow | MGD | -- | Continuous |
| Acute toxicity | TUa | Grab | + |
| Chronic toxicity | TUc | Grab | + |

+	Acute or chronic toxicity shall be conducted if the combined 	monitoring for acute or chronic toxicity demonstrates a 	toxic response.

F.   LOW VOLUME WASTES MONITORING

The following shall constitute the low volume wastes monitoring program for each low volume waste stream:

| Parameter | Units | Sample Type | Minimum Reporting Frequency |
| --- | --- | --- | --- |
| Flow | MGD | -- | Monthly |
| Total Suspended Solids | mg/L | Grab | Monthly |
| Grease and Oil | mg/L | Grab | Monthly |

G.	METAL CLEANING WASTES MONITORING

The following shall constitute the metal cleaning wastes 	monitoring program for each metal cleaning waste stream:

| Parameter | Units | Sample Type | Minimum Reporting Frequency* |
| --- | --- | --- | --- |
| Total suspended solids | mg/L | Grab | Prior to Discharge |
| Oil & Grease | mg/L | Grab | Prior to Discharge |
| Copper, total | mg/L | Grab | Prior to Discharge |
| Iron, total | mg/L | Grab | Prior to Discharge |

* After initial discharge, monitoring shall be weekly.

H.	NON-CHEMICAL METAL CLEANING MONITORING

The following shall constitute the metal cleaning wastes monitoring program for each metal cleaning waste stream:

| Parameter | Units | Sample Type | Minimum Reporting Frequency* |
| --- | --- | --- | --- |
| Total suspended solids | mg/L | Grab | Prior to Discharge |
| Oil & Grease | mg/L | Grab | Prior to Discharge |
| Copper, total | mg/L | Grab | Prior to Discharge |
| Iron, total | mg/L | Grab | Prior to Discharge |

* After initial discharge, monitoring shall be weekly.

I.	FISH HANDLING SYSTEM MONITORING

As required for evaluating the studies in Finding No. 64 the discharger shall submit reports describing the operation of the fish handling systems for Units 2 and 3.  The Executive Officer may request additional monitoring after review of the reports and consultation with representatives of the State Department of Fish and Game.

J.	RECEIVING WATER MONITORING

Receiving water monitoring shall be conducted as specified below.  Station location, sampling, sample preservation and analysis, when not specified, shall be by methods described in the discharger's previous annual reports (Marine Environmental Analysis and Interpretation, San Onofre Nuclear Generating Station, 1990, 1991 and 1992 Annual Reports) submitted to the Regional Board.  A summary of the monitoring program is presented in Table 1, and station locations for the various study elements are shown in

Figures 1A through 1D.

The following study elements shall represent the receiving water monitoring program.

1.	Continuous Temperature Monitoring

Continuously recording thermographs will be employed at three stations (Figure 1A).  Measurements will be obtained from the surface, 5 m, 10 m and near-bottom.  Measurements will be reported as hourly data.

2.	Turbidity

Quarterly aerial photographic surveys will be conducted in the area of the Units 2 and 3 diffuser system.

3.	Fish Populations

Quarterly trawling surveys will be conducted at three stations (Figure 1B) located offshore of San Mateo Point, SONGS and Don Light.  Daylight sampling by otter trawl will be accomplished at the 20, 40 and 60 ft. isobaths at each station.  Each trawl will be of five minute duration.  Collected fishes will be identified and enumerated, and sex determined for selected species.

4.	Kelp Densities

Individual giant kelp plants and the number of associated stipes greater than 2 m will be counted tri-annually at six fixed sampling sites located in the San Onofre Kelp (Figure 1C).  The composition of the substrate will be qualitatively described.  Additional substrate and percent cover information will be collected.

A random sampling of the 100 m2 will be conducted semi-annually to enumerate giant kelp, and a qualitative estimate of percent sand, cobble and boulder made.

5.	Kelp Bed Monitoring

Kelp bed monitoring is conducted to assess the extent to which the discharge of wastes may affect the areal extent and health of coastal kelp beds.  The discharger shall participate with other ocean dischargers in the San Diego Region in an annual regional kelp bed photographic survey.  Kelp beds shall be monitored annually by means of vertical aerial infrared photography to determine the maximum areal extent of the region's coastal kelp beds within the calendar year.  Surveys shall be conducted as close as possible to the time when kelp bed canopies cover the greatest area, which ordinarily occurs in August or September in the San Diego Region.  The entire San Diego Region coastline, from the International Boundary to the San Diego Region/Santa Ana Region boundary, shall be photographed on the same day.  The date of each annual survey shall be approved by a Regional Board staff.  (Verbal approval will be sufficient, so that the survey will not be delayed while written approval is prepared and distributed.)

The images produced by the surveys shall be presented in the form of a 1:24,000 scale photo-mosaic of the entire San Diego Region coastline.  Onshore reference points, locations of all ocean outfalls and diffusers, and the 30-foot (MLLW) and 60-foot (MLLW) depth contours shall be shown.

The area/extent of the various kelp beds photographed in each survey shall be compared to that noted in surveys of previous years.  Any significant losses which persist for more than one year shall be investigated by divers to determine the probable reason for the loss.

6.	Temperature Profiles

Temperature profiles from the surface to the bottom will be measured quarterly at 29 stations (Figure 1D).

7.	Transmissometer Profiles

Surface to bottom profiles of light transmittance will be conducted quarterly from 29 stations (Figure 1D).

8.	Water Quality Measurements

Water quality parameters, dissolved oxygen and hydrogen ion concentration, will be measured quarterly at the surface of ten stations (Figure 1D).

REPORTING

(a)	A report containing detailed analyses of the previous year's receiving water monitoring data shall be submitted by July 30 of each year.  Each section of the report shall contain a graphical and written summary of historical data with the goal of displaying long term trends.

(b)	The annual summary report requirement in Section K of this Monitoring and Reporting Program will not apply to Receiving Water Monitoring.

K.	ANNUAL SUMMARY OF MONITORING DATA

By January 30 of each year, the discharger shall submit an annual report to the Executive Officer.  The report shall contain both tabular and graphical summaries of the monitoring data obtained during the previous year.  In addition, the discharger shall discuss the compliance record and the corrective actions taken or planned which may be needed to bring the discharge into full compliance with the waste discharge requirements of this Order.

L.	MONITORING REPORT SCHEDULE

Monitoring reports shall be submitted to the Executive Officer according to the dates in the following schedule:

Monitoring Frequency			Report Due

Continuous, Daily, Weekly		By the 30th of

or Monthly					following month

Quarterly						January 30, April 30,

July 30, October 30

Semiannually					January 30, July 30

Annually						January 30 (Effluent)

July 30 (Receiving Water)

TABLE 1.  SUMMARY OF NPDES RECEIVING WATER MONITORING PROGRAM

STUDY ELEMENT     STATION LOCATION    FREQUENCY       SAMPLE TYPE

MONITORING

Continuous         C2S/F2S/C22S        Continuous       Remote

Temperature

Turbidity          Units               Quarterly        Aerial

2 and 3 Diffusers                    Photos

Fish Populations   M, San Mateo;       Quarterly        Trawl

S, San Onofre;

D, Don Light

SPECIAL STUDIES

Temperature

Profiles           F2ON/J8N/J4N        Quarterly        Grab

J2N/JO/J2S/

J4S/J8S/M8N/

M4N/M2N/MO/

M2S/M4S/M8S/

F2N/F2S/F22S/

F24S/F26S/H2N/

HO/H2S

Transmissometer    See Temp Location   Quarterly        Grab

Profiles

Water Quality,     J2S/J2N/J4S/F22S    Quarterly        Grab

pH and DO

REPORTING          N/A	              Annual

CALIFORNIA REGIONAL WATER QUALITY CONTROL BOARD

SAN DIEGO REGION

Endnote references for Monitoring and Reporting Program No. 99-47 (NPDES NO. CA0108073), SOUTHERN CALIFORNIA EDISON COMPANY, SAN ONOFRE NUCLEAR GENERATING STATION, UNIT 2, SAN DIEGO COUNTY.

1.	For fish length, where up to 125 individuals of a species are removed, the "representative sample" shall consist of all the individuals removed. Where more than 125 individuals of a species are removed, the "representative sample" shall consist of not less than 125 individuals.  For determination of fish sex, the procedure shall be the same as for fish length, except the number of individuals shall be 50.

2.	Composite samples taken for combined discharge monitoring 	must be taken during 24 hour intervals where inputs from 	in-plant waste streams is maximized, especially full flow 	condensate polishing demineralizer system regenerants and 	high flow make-up demineralizer regenerants.

3.	Combined discharge monitoring shall be conducted at a point in the circulating water system downstream of the condenser, downstream of the point(s) at which the component cooling and turbine plant cooling water streams reenter the circulating water stream, and downstream of the point(s) at which all in-plant waste streams, enter the circulating water stream.  Combined discharge samples shall be collected immediately following collection of cooling water intake samples.

4.	The discharger may at their option meet this limitation as a total chromium limitation.

5.	Samples shall be collected and analyzed for total residual chlorine and free available chlorine at times when the concentration of total residual chlorine and free available chlorine in the combined discharge is greatest.  The times of uninterrupted chlorine discharges on the days the samples are collected and the times at which samples are collected shall be reported.

6.	HCH shall mean the sum of the alpha, beta, gamma (lindane) and delta isomers of hexachlorocyclohexane.

7.	Toxicity concentration shall be measured in the following manner.

a.  Acute Toxicity (TUa)

TUa = 100/96-hr LC 50%

Compliance with acute toxicity will be expressed as TUa, which equals 100/NOAEC.  No Observable Adverse Effect Concentration (NOAEC) is the highest concentration at which survival is not significantly different from the control in a 96-hour static renewal test.

b.	Chronic Toxicity Testing

TUc  =  100/NOEC

Compliance with chronic toxicity will be expressed as TUc, which equals 100/NOEC.  NOEC (No Observed Effect Concentration) is the highest concentration of toxicant, in terms of percent effluent, to which the test organisms are exposed that causes no observable adverse effect.  The chronic toxicity limitation is:  1) a monthly median of 1.0 TUc, or 2) any one test result with greater than a 50% toxic effect.

8.	Copies of all SCE reports to the Nuclear Regulatory Commission pertaining to monitoring of radioactive materials in wastewater released from SONGS and radiological environmental monitoring shall be transmitted to the Regional Board.

9.	Temperature shall be recorded at a minimum frequency of once every two hours.  The average and maximum temperature for each 24-hour period shall be reported.  Insignificant figures shall be rounded to the nearest significant figures. The daily average difference (T) and the maximum daily difference (Tm) between the intake and discharge temperatures shall also be reported.

10.	For the purposes of monitoring, the following shall be 	considered courses of in-plant waste streams:

a.	seawater pumps bearing flush water

b.	storm drains

c.	screen wash

d.	domestic wastewater treatment plants

e.	low volume wastes (as listed in Finding No. 3126 of the 			Order)

11.	Grab samples and individual in-plant waste streams shall be 	collected and composited on a flow-weighted basis for 	analysis.  Measurements or estimates of flows of individual 	in-plant waste streams used as a basis for compositing shall 	be reported.

Ordered by ________________________

John H. Robertus

Executive Officer

Date Ordered: August 11, 1999