CALIFORNIA REGIONAL WATER QUALITY CONTROL BOARD

SAN DIEGO REGION

ORDER NO. 99-47

NPDES PERMIT NO. CA0108073

WASTE DISCHARGE REQUIREMENTS

FOR

SOUTHERN CALIFORNIA EDISON COMPANY

SAN ONOFRE NUCLEAR GENERATING STATION, UNIT 2

SAN DIEGO COUNTY

Table of Contents

Findings	.	.	.	.	.	.	.	.	.	.	.	.	.	.	.	.	.	.	1

A. Prohibitions	.	.	.	.	.	.	.	.	.	.	.	.	.	.	. 17

B.	Discharge Specifications	.	.	.	.	.	.	.	.	.	.	. 18

C.	Heat Treatment Discharge Specifications	.	.	.	.	.	. 31

D.	Receiving Water Limitations	.	.	.	.	.	.	.	.	.	. 33

E.	Provisions	.	.	.	.	.	.	.	.	.	.	.	.	.	.	.	. 38

F.	Reporting Requirements	.	.	.	.	.	.	.	.	.	.	.	. 45

G.	Notifications	.	.	.	.	.	.	.	.	.	.	.	.	.	.	. 50

Appendix A: Endnote References	.	.	.	.	.	.	.	.	.	. 52

Attachment A:	Site Map	.	.	.	.	.	.	.	.	.	.	.	.	. 57

Attachment B:	Flow Diagram	.	.	.	.	.	.	.	.	.	.	. 58

Attachment C:	Intermittent and Seasonal Discharges	.	.	. 59

Attachment D:	Heat Treatment Decision Chart	.	.	.	.	.	. 60

Attachment E:	Time-Temperature Mortality Curve	.	.	.	.	. 61

Attachment F:	Basin Plan Discharge Prohibitions	.	.	.	. 62

Attachment G:	Standard Provisions	.	.	.	.	.	.	.	.	. 65

Attachment H:	Sections of 40 CFR Incorporated by Reference	. 71

The California Regional Water Quality Control Board, San Diego Region (Hereinafter Regional Board), finds That:

1.	On March 4, 1985, The Regional Board adopted Order No. 85-11, 	National Pollutant Discharge Elimination System (NPDES) No. 	CA0108073, Waste Discharge requirements for Southern 	California Edison Company, San Onofre Nuclear Generating 	Station, Unit 2, San Diego County.  Order No. 85-11 expired on 	March 14, 1990, but was administratively extended until 	adoption of this Order.

2.	On September 14, 1989, Southern California Edison Company 	(SCE) submitted a complete report of waste discharge (RWD), 	dated September 13, 1989, in application for renewal of the 	NPDES permit for San Onofre Nuclear Generating Station (SONGS) 	Unit 2.  SCE submitted amendments to the original application 	dated November 3, 1989, August 22, 1991, December 5, 1991, 	June 2, 1993, October 27, 1993, November 18, 1993, July 5, 	1994 and July 20, 1994.

3.	On August 11, 1994, The Regional Board adopted Order No. 94-	49, NPDES No. CA0108073, Waste Discharge requirements for 	Southern California Edison Company, San Onofre Nuclear 	Generating Station, Unit 2, San Diego County.

4.	Order No. 94-49 was modified through addenda three times 	during the 5 year period of the permit.  Addendum No. 1 	contained effluent limitations and monitoring requirements for 	metal cleaning waste discharges and was adopted on January 9, 	1997.  Addendum No. 2 raised the delta temperature (T) 	effluent limitation from 20F to 25F and was adopted by the 	Regional Board on February 11, 1998.  Addendum No. 2 was 	affirmed by State Board Resolution No. 99-028 that gave the 	requisite approval for the exception to the California Thermal 	Plan.  This State Board resolution was adopted April 14, 1999.  	Addendum No. 3 contained effluent limitations and monitoring 	requirements for non-chemical cleaning waste discharges and 	was adopted on December 16, 1998.

5.	On February 11, 1999, SCE submitted an incomplete NPDES permit 	renewal application.  The application contained a form 200 	Report of Waste Discharge, a US Environmental Protection 	Agency (USEPA) form 2C, and a USEPA form 1.  In addition, SCE 	asked for several changes to be incorporated into the new 	permit, these include: a reduction in the monitoring frequency 	for toxicity, a reduction in the fish trawling monitoring 	frequency, a reduction in the frequency 	for offshore kelp 	monitoring, and rewording of the heat treatment language.  SCE 	reported the following information in form 2C:

| Pollutant | Units | Influent Concentration from 1989 Application | Effluent Concentration from 1999 application |
| --- | --- | --- | --- |
| Total Suspended Solids (TSS) | mg/l | 6.8 | 7.2 |
| Ammonia (as N) | mg/l | 1.4 | 2.9 |
| Bromide | ug/l | 102 | 143 |
| Chlorine, Total Residual | ug/l | --- | 180 |
| Color | color units | 3 | 4 |
| Boron, Total | mg/l | 4.1 | 4.3 |
| Magnesium, Total | mg/l | 1247 | 1306 |

6.	On March 16, 1999, Regional Board staff sent a letter to SCE requesting the missing information in the permit application.  On May 18, 1999, staff received an information packet containing most of the required information.  However, the waste characterization of the fish return system discharge and across the beach discharge was not included.

7.	On June 10, 1999, Regional Board staff sent a letter to SCE requesting the missing waste characterization data from outfalls 4 and 5.  In addition, the staff’s letter requested material safety data sheets for several chemicals used at SCE, a characterization of chemical use for several chemicals, sampling data for hydrazine and ethanolamine, and cost information for the use of down-scanning and side-scanning sonar in receiving water monitoring.  SCE submitted the required data in two mailings.  Regional board staff received the mailings on July 14, 1999 and July 28, 1999.

8.	SONGS is a nuclear-fueled electrical power generating facility located in San Diego County immediately adjacent to the Pacific Ocean, approximately two and one-half miles southeast of San Mateo Point, within the boundaries of the United States Marine Corps Base, Camp Pendleton.  SONGS is located in Section 24, T9S, R7W, SBBM, approximately two and one-half miles southeast of the City of San Clemente and approximately 12 miles northwest of the City of Oceanside.  Unit 2 has an electrical output of 1087 MW.  Unit 2 began commercial operation on August 18, 1983.

SONGS Unit 2 has the following discharges:

9.	A combined discharge of once-through cooling water and other wastes through the SONGS Unit 2 Outfall;

10.A periodic fish return system discharge of circulating seawater, without in-plant wastes, through the SONGS Units 2 and 3 Fish Return System Outfall; and,

11.A periodic discharge of once-through cooling water, without in-plant wastes, for emergency cooling and cooling for certain maintenance activities at an Across-the-Beach discharge point.

12.Attachment A is a site map of the SONGS facilities.

13.Attachment B is a flow diagram of discharged wastes for Unit 2.

14.Attachment C is a table of intermittent discharges and respective flows for Unit 2.

15.SONGS Unit 2 is owned by SCE, San Diego Gas and Electric Company (SDG&E) and the Cities of Anaheim and Riverside.  However, SCE is primarily responsible for the operation of SONGS Unit 2.  Consequently this permit is issued to SCE, pursuant to the United States Environmental Protection Agency (USEPA) Consolidated Permit Regulations, 40 CFR Part 122.4(b).

16.SONGS Unit 2 uses a once-through ocean water cooling system.  The once-through cooling water stream for Unit 2 has a maximum flowrate of 1218.6 million gallons per day (MGD) and a normal operational temperature increase across the condensers of 19.2F.  The intake is located 3,183 ft. offshore in 32 ft. of water.  The Unit 2 outfall diffuser extends from 5,888 ft. to 8,350 ft. offshore and ranges in depth from 39 ft. to 49 ft.  The Unit 2 outfall has a point of discharge located at Latitude 33 20’ 55.84" North and Longitude 117 34’ 13.5" West.

17.The Unit 2 screenwells contain a fish guidance and return system.  The fish handling system consists of a series of vertical louvers that guide entrapped fish to a large quiet-water area in the screenwell, fish elevators that remove the fish from the screenwells, and a 4 ft. diameter water conduit that returns fish to the ocean, depositing them 1,900 ft. offshore.  The fish return conduit is common to both Units 2 and 3 and is referred to as the SONGS Units 2 and 3 Fish Return System Outfall.

18.In order to control the growth of slime-forming organisms on condenser internal surfaces, the once-through condenser cooling water is currently brominated/chlorinated at the condenser inlet about twice per day.  Each injection period is approximately 50 minutes long.

19.The maximum discharge flowrate from the SONGS Unit 2 Outfall is 1286.9 MGD and consists of the following waste streams (maximum flowrates are indicated in parentheses):

a. Once-through condenser cooling water (1218.6 MGD)

b. Saltwater cooling system (49.0 MGD)

c.	Sea water pumps bearing flush water (0.172 MGD)

d.	Storm drains (0.168 MGD)

f.	Screen wash (7.2 MGD)

g.	Domestic wastewater treatment plants (0.145 MGD)

h.	Low volume wastes (11.61 MGD)

These wastestreams are described in the following findings.

20.Once-through condenser cooling water contains waste heat and residual chlorine or bromine and may contain metals leached from piping.  A maximum flowrate of 1218.6 MGD of once-through condenser cooling water is discharged through the SONGS Unit 2 Outfall.

21.The saltwater cooling system (SWCS) uses ocean water to remove heat from the component cooling water system (CCWS) and the turbine plant cooling water (TPCW) system.  The CCWS is a closed loop system designed to remove heat from various reactor auxiliary systems.  The CCWS provides a radioactivity monitored intermediate barrier between the reactor auxiliary systems and the SWCS.  The TPCW is a closed loop cooling system with a primary function to remove waste heat from the components of the steam plant auxiliary systems.  As shown in attachment B, the SWCS flow is withdrawn from and returned to the once-through condenser cooling water stream.  The SWCS is chlorinated to control biofouling.  A maximum flowrate of 49.0 MGD is discharged from the saltwater cooling system through the SONGS Unit 2 Outfall.  During periods of discharge structure maintenance and emergencies, the SWCS discharges at the Across-the-Beach discharge point.

22.Sea water pump bearings are lubricated by a once-through flow of domestic water.  Of the total 0.172 MGD of sea water pumps bearing flush water discharged, 0.070 MGD is directed to the intake structure sump and 0.102 MGD to the once-through condenser cooling water stream.

23.Storm drains collect dewatering of groundwater, rainfall runoff, auxiliary boiler drain down and hose-down water from outside areas at the SONGS Unit 2 facility.  Water entering storm drains is discharged directly to the once-through condenser cooling water stream.  Storm drain flows may be virtually negligible in the absence of rainfall.  During the rainy season, storm drain flowrates average approximately 0.074 MGD.  A maximum flowrate of 0.168 MGD is discharged from storm drains to the SONGS Unit 2 Outfall.

24.The traveling screens and bars provide a method to remove marine life and debris from the once-through cooling water.  Each of two screen wash pumps delivers a maximum flowrate of 2,500 gallons per minute for washing the traveling screens, traveling bar screens, and fish elevator.  A maximum screen wash flowrate of 7.2 MGD is withdrawn from and returned (recirculated) to the once-through condenser cooling water stream.

25.Domestic sewage generated at SONGS is treated at either the SONGS Unit 1 sewage treatment plant or the Mesa Facility Complex sewage treatment plant.  The effluents from both facilities are discharged to the SONGS Unit 1 Outfall, SONGS Unit 2 Outfall, or SONGS Unit 3 Outfall, depending on operating conditions.  The maximum effluent flowrate from the SONGS Unit 1 sewage treatment plant is 0.10 MGD.  The maximum effluent flowrate from the Mesa Facility Complex sewage treatment plant is 0.045 MGD.

26.Low volume waste streams include the following (maximum flowrates are indicated in parentheses):

a.	Thermophilic digester (0.010 MGD)

b.	Condenser hotwell overboard (7.20 MGD)

c.	Steam generator blowdown (0.720 MGD)

d.	Blowdown processing system demineralizer regenerants (0.085 MGD)

e.	Full flow condensate polishing demineralizer regenerants (1.40 MGD)

f.	Makeup demineralizer regenerants (0.670 MGD)

g.	Radwaste system (0.432 MGD)

h.	Building sumps (0.800 MGD)

i.	Intake structure sump (0.288 MGD)

The low volume waste streams identified above are described in the following findings.

27.SCE is proposing to install and operate a thermophilic digester which would be used to treat kelp debris, dead fish, sludge from both sewage treatment plants and kitchen grease.  SCE reports that use of a thermophilic digester would reduce the solid waste disposal needs of the SONGS facilities.  SCE may begin operation of a thermophilic digester sometime during the life of this Order.  A maximum flowrate of 0.010 MGD of supernatant from the thermophilic digester would be discharged to the influent of the SONGS Unit 1 Sewage Treatment Plant.

28.A condenser hotwell overboard discharge is necessary if leaks are detected in the condenser or during start-up of the unit.  The condenser hotwell overboard discharges a maximum flowrate of 7.20 MGD to SONGS Unit 2 Outfall.

29.The steam generator provides steam to the turbine, utilizing heat from the reactor primary cooling system.  Hydrazine, and ammonia and ethanolamine are used to control the oxygen concentration and pH, respectively, of the demineralized feedwater which comes from the demineralizer.  They form gaseous products, mainly nitrogen, which do not significantly affect the chemical characteristics of the blowdown.  During normal operation, chemicals, such as ammonium hydroxide, are added to control pH.  The maximum steam generator blowdown discharge flowrate to the SONGS Unit 2 Outfall is 0.720 MGD.

30.Steam generator blowdown not discharged directly to the once-through cooling water stream flows to the steam generator blowdown processing system (BPS) which functions to demineralize the steam generator blowdown and provide high quality condensate back to the main condenser.  The BPS contains units for filtration and ion-exchange.  Only under unusual circumstances, such as a saltwater leak, are the ion-exchangers put into operation.  This side stream demineralizer is regenerated and the spent regenerants are neutralized to acceptable pH limits prior to discharge to the once-through condenser cooling water stream.  The maximum blowdown processsing system demineralizer regenerants flowrate to the SONGS Unit 2 Outfall is 0.085 MGD.

31.Steam, upon passing the turbine, is condensed back to water.  The condensate is demineralized prior to returning to the steam generator.  The full flow condensate polishing demineralizer (FFCPD) system is designed to remove positive and negative ions entering the system from small leaks which may develop in the main condenser and associated piping.  The spent regenerants (sulfuric acid and caustic soda) are neutralized, settled, and filtered to acceptable limits prior to discharge.  The maximum wastewater flowrate from the full flow condensate polishing demineralizer system to the SONGS Unit 2 Outfall is 1.40 MGD.

32.The makeup demineralizer (MUD) system produces deionized water for various in-plant systems and is common to Units 1, 2, and 3.  The source water for the MUD is potable water purchased from the Tri-Cities Municipal Water District.  The ion exchange resins are routinely regenerated, with the wastewater (acidic and alkali) flowing to a neutralization tank.  The pH is then adjusted to acceptable limits by the addition of sulfuric acid or caustic soda.  Upon neutralization the regeneration wastewater is then discharged through either the SONGS Unit 2 Outfall, or the SONGS Unit 3 Outfall.  A reverse osmosis (RO) unit may be used to supplement the ion exchange system; producing additional make-up water and discharging brine via the MUD system piping.  The maximum makeup demineralizer regenerants flowrate is 0.670 MGD.

33.The radioactive waste system provides radiological waste management.  The system receives wastewater from reactor coolant systems, chemical and volume control systems, and minor flows from equipment leaks and drains, laboratory drains, personnel decontamination showers, and floor drains.  Treatment facilities consist of a series of surge tanks, demineralizers, filters, monitor tanks, flash tanks, and gas strippers.  The radiological wastewater is treated to acceptable radiological limits established by the U.S. Nuclear Regulatory Commission for discharge or plant recycle.  The maximum wastewater flowrate from the radwaste system to the SONGS Unit 2 Outfall is 0.432 MGD.  Radwaste from Unit 1 may be combined with Unit 2 radwaste and discharged out the Unit 2 outfall.

34.With the exception of the intake structure sump, which discharges directly into the intake structure, and the Full Flow Condensate Polishing Demineralizer (FFCPD) area, which discharges to the FFCPD sumps, wastewater entering all drains labeled by SCE as "nonradioactive" flow by gravity to building sumps.  From there, the wastewater is pumped to the Unit 2 and Unit 3 oily waste sumps.  Under normal operating conditions, both sumps are treated in the Unit 2 oil/water separator and wastewater is discharged out the Unit 2 outfall.  In the case of a Unit 2 outage, all waste is treated in the Unit 3 flocculator and is discharged out the Unit 3 outfall.  The maximum wastewater flowrate from building sumps to the SONGS Unit 2 Outfall is 0.800 MGD.

35.The intake structure sump receives a portion of the sea water pumps bearing flush water and flows from sea water drains.  The water in the intake structure sump is then pumped to the once-through cooling water stream.  The maximum intake structure sump discharge flowrate to the SONGS Unit 2 Outfall is 0.288 MGD.

36.On May 18, 1972, the State Water Resources Control Board (State Board) adopted the "Water Quality Control Plan for Control of Temperature in the Coastal and Interstate Waters and Enclosed Bays and Estuaries of California," hereinafter called the Thermal plan.  Water Quality Objective 3B(3) of the Thermal Plan Provides:

"The maximum temperature of thermal waste discharges shall not exceed the natural temperature of receiving waters by more than 20F."

37.On February 11, 1998, the Regional Board approved SCE’s request for a 5 degree increase in the T effluent limitation for the Unit Nos. 2 and 3 outfalls.  This required an exception from the Thermal Plan requirements and thus approval by the State Board.  On May 5, 1999, the State Board gave final approval and affirmed the Regional Board’s decision.  As part of this approval, both the State and Regional Boards acknowledged compliance with Section 316(a) of the Clean Water Act.

38.On July 31, 1972, the Regional Board adopted Order No. 72-26.  The Order granted an exception from Objective 3B(3) of the Thermal Plan for heat treatment to control marine fouling organisms in the intake and discharge conduits of SONGS Units 2 and 3.  The Regional Board proposed the following language as a substitute for Objective 3B(3):

"The companies may raise the temperature of the cooling water discharge from planned Units 2 and 3 of the San Onofre Nuclear Generating Station to not more than 125F for periods of not more than two hours once each five week period for each unit, for purposes of control of marine organism growth in the cooling water system only:"

and

"Thermal treatment shall be done in such a manner and under such conditions that loss of fish and other marine life is eliminated or minimized, and effects upon ocean water quality is minimized."

39.The Regional Board, in Order No. 72-26, requested State Board concurrence with the exception to the Thermal Plan.

40.On February 15, 1973, the State Board adopted Order No. 73-5, which concurred conditionally with the Regional Board Order No. 72-26.  Under the conditions contained in Order No. 73-5, SCE and SDG&E were required to complete certain studies.

41.On March 6, 1973, the conditions contained in State Board Order No. 73-5 were incorporated into Regional Board Order No. 72-26 by Addendum No. 1 to Regional Board Order No. 72-26.

42.On January 31, 1979, SCE submitted final reports for the studies required in Order No. 73-5 and Regional Board Order No. 72-26 to the State and Regional Boards, SCE requested that these reports be approved as fulfilling the conditions established in State Board Order No. 73-5 and Regional Board Order No. 72-26.  SCE also submitted proposed heat treatment operating conditions.

43.After reviewing the reports submitted by SCE and other pertinent data, the State Board concluded that the reports fulfilled the conditions set forth in Order No. 73-5 and Regional Board order No. 72-26.

44.The State Board further found that the heat treatment operating conditions proposed by SCE would assure the protection and propagation of a balanced, indigenous population of shellfish, fish, and wildlife within the meaning of Section 316(a) of the Clean Water Act.

45.On December 18, 1980, the State Board adopted Resolution No. 80-95 that approved the completed heat treatment studies and proposed heat treatment operating criteria for SONGS Units 2 and 3.  Resolution No. 80-95 required that the proposed heat treatment operating conditions as amended be incorporated into the operating procedures and waste discharge requirements for Units 2 and 3.

46.The State Board adopted a revised "Water Quality Control Plan for Ocean Waters of California" (Ocean Plan) on July 23, 1997.  The Ocean Plan identifies the following beneficial uses of state ocean waters to be protected:

a.	Industrial water supply;

b.	Water contact recreation;

c.	Non-contact water recreation;

d.	Aesthetic enjoyment;

e.	Navigation;

f.	Ocean commercial and sport fishing;

g.	Mariculture;

h.	Preservation and enhancement of Areas of Special Biological i.	Significance;

j.	Preservation of rare and endangered species;

k.	Marine habitat;

l.	Fish migration;

m.	Fish spawning; and,

n.	Shellfish harvesting.

47.In order to protect these beneficial uses, the Ocean plan establishes water quality objectives, general requirements for management of waste discharges to the ocean, quality requirements for waste discharges, discharge prohibitions, and general provisions.

48.The Ocean Plan establishes a procedure for determining effluent limitations that are based on the minimum initial dilution of a discharge by the receiving ocean waters.  The State Board has issued a document entitled Water Quality Control Plan, Table B Guidelines, Ocean Waters of California, 1978 to assist in implementing the Ocean Plan.  The Table B guidelines describe two numerical models for use in estimating the minimum initial dilution of a discharge.  If the models described in the Table B Guidelines are not applicable, a discharger may propose another numerical model or use the results of a site-specific physical modeling study.  Neither of the models described in the Table B guidelines is applicable to the SONGS Unit 2 discharge.

49.The Ocean Plan defines minimum initial dilution for submerged discharges as complete when the diluting wastewater ceases to rise in the water column and first begins to spread horizontally.  For the purposes of the Ocean Plan, minimum initial dilution is the lowest average initial dilution within any single month of the year.  Dilution estimates shall be based on observed waste flow characteristics, observed receiving water density structure, and the assumption that no currents, of sufficient strength to influence the initial dilution process, flow across the discharge structure.

50.On November 15, 1974, the California Institute of Technology submitted a report to SCE titled "Interpretation of results from Hydraulic Modeling of Thermal Outfall Diffusers for the San Onofre Nuclear Power Plant."  The report concluded that the discharge diffuser, as designed, would induce an offshore current.  In addition, the report stated that in the absence of surface cooling and no ambient current, the initial dilution is about 10.

51.On July 18, 1979, SCE requested that the State Board staff approve estimated initial dilution factors for those discharge structures generally described as "offshore submerged."  These dilution factors were estimated utilizing the "flux-weighted-average" dilution approach developed by the California Institute of Technology.  On March 13, 1980, the State Board staff agreed with SCE’s approach for estimating initial dilution for "offshore submerged" discharges and approved the use of these calculated initial dilution factors when issuing future NPDES permits for these discharges.  The minimum probable initial dilution, as defined by the Ocean Plan, for the SONGS Unit 2 Outfall is 10.

52.The Ocean Plan requires that waste be discharged a sufficient distance from areas designated as being of special biological significance to assure maintenance of natural water quality conditions in such areas.  Heisler Park Ecological Reserve, approximately 20 miles northwest of SONGS Unit 2, is the closest designated Area of Special Biological Significance to the SONGS Unit 2 discharge.

53.The Comprehensive Water Quality Control Plan Report, San Diego Basin (9) (Basin Plan) was adopted by the Regional Board on March 17, 1975, and approved by the State Board on March 20, 1975.  Subsequent revisions to the Basin Plan have also been adopted by the Regional Board and approved by the State Board.  The most recent revisions were adopted by the Regional Board on September 8, 1994 and affirmed by the State Board on December 13, 1994.

54.The Basin Plan identifies the following beneficial uses of the coastal waters of the Pacific Ocean:

a.	Industrial Service Supply;

b.	Navigation;

c.	Water Contact Water Recreation;

d.	Non-Contact Water Recreation;

e.	Ocean Commercial and Sport Fishing;

f.	Preservation of Areas of Special Biological Significance;

g.	Preservation of Rare and Endangered Species;

h.	Marine Habitat;

i.	Fish Migration;

j.	Shellfish Harvesting;

k.	Wildlife Habitat;

l.	Fish Spawning; and

m.	Aquaculture.

55.Effluent limitations, national standards of performance, and toxic and pretreatment effluent standards established pursuant to Section 301, 302, 303(d), 304, 306, 307, 316(b) and 403 of the Clean Water Act and amendments thereto are applicable to the discharge.

56.On November 19, 1982, the USEPA promulgated effluent guidelines and standards for discharges from the steam-electric power generating point source category.  The guidelines establish effluent limitation guidelines, pretreatment standards, and new source performance standards and are contained in 40 CFR Parts 125 and 423.  The best practicable control technology currently available (BPT) and best available technology economically achievable (BAT) effluent limitations promulgated by USEPA to regulate pollutants for the steam electric power generating point source category are applicable.

57.On February 20, 1974, the California Coastal Zone Conservation Commission created the Marine Review Committee (MRC) as a permit condition for the construction of Units 2 and 3 and directed the MRC to analyze the effects of Units 2 and 3 on the marine environment.  Within the final study report issued by the MRC (MRC, 1989a), the MRC estimated that the average level of natural light at the bottom at stations down coast from SONGS Units 2 and 3 outfall diffusers was lowered by 6-16% relative to the level that would occur in the absence of SONGS during a downcoast current.  The MRC report states that this finding is statistically significant at the 95% confidence level.

58.The California Coastal Commission has adopted a resolution acknowledging the MRC findings and has conditioned SCE’s coastal permit to require mitigation that will offset the marine resource impacts which have been caused by SONGS Units 2 and 3 as identified by the MRC.  These efforts are ongoing.

59.On April 18, 1983, Regional Board staff accompanied representatives of SCE on a helicopter flight over the SONGS Units 1, 2, and 3 Outfalls.  Discoloration over SONGS Units 1 and 3 Outfalls were visible, apparently as a result of the operation of SONGS Unit 1 and Unit 3 circulating water pumps.  Regional Board staff did not view any discoloration over the SONGS Unit 2 outfall.  However, Regional Board staff believes that the SONGS Unit 2 discharge may also create a turbidity plume in the same manner as SONGS Units 1 and 3.  The turbidity of the SONGS Unit 2 discharge has the potential of adversely affecting the marine biota in the vicinity of the discharge.  As part of the previous permit, SCE was required to conduct a special 1-year study measuring the turbidity of the Unit 2(3) intake and discharge for one year.  On May 6, 1996, SCE submitted the required study.  The study concluded that in-plant waste streams at SONGS do not contribute a significant amount of turbidity to the combined discharge, and that there is a large natural variability in the turbidity of the SONGS discharge.

60.The Ocean Plan requires that "natural light shall not be significantly reduced at any point outside the initial dilution zone as the result of the discharge of waste."

61.On February 10, 1992, the Regional Board held a special session to consider the issue of possible noncompliance with the NPDES permits for SONGS Units 2 and 3.  The non-compliance was based on Ocean Plan violations of transmitted light limitations and impacts to the Marine environment.  The recommendations were based on extensive studies done on behalf of the MRC.  The Regional Board determined that the conflicting interpretations of the available data made the compliance status of SONGS Units 2 and 3 uncertain.  The Regional Board concluded that the evidence was not sufficient to support a finding of noncompliance.

62.During the approval of the Thermal Plan exception outlined in Finding 37, the California Coastal Commission (CCC) sent several letters to Regional Board staff requesting that sonar techniques be used to monitor the impacts to kelp.  In response, SCE provided information supporting their position that sonar monitoring techniques for the kelp bed were duplicative and unnecessary.

63.Under previous permits, SCE was required to conduct side-scanning sonar surveys of the kelp beds in San Onofre and San Mateo.  This began in 1974 and continued until the requirement was waived from the NPDES permit in 1994.  Downlooking sonar was used from early 1982 until 1994.  Apparently, SCE continued to utilize sonar methods until 1997, despite the relaxed permit requirements.  The monitoring and reporting program to this order does not require sonar based kelp monitoring.

64.Clean Water Act Section 316(b) requires that the location, design, construction and capacity of cooling water intake structures reflect the best technology available for minimizing adverse environmental impact.  On July 29, 1988, SCE submitted a report entitled, "Marine Environmental Analysis and Interpretation, Report on 1987 Data, San Onofre Nuclear Generating Station."  Chapter 10 of that report contains the results of a study designed to demonstrate conformance with Section 316(b) for SONGS Units 2 and 3.  The study consisted of determining entrainment, impingement and field populations of fishes.  The analysis evaluated the losses attributed to Units 2 and 3 intake structures as compared to offshore population densities and distributions.

65.Clean Water Act Section 316(b) compliance was further analyzed in 1994.  The Science Applications International Corporation Submitted a report titled "Review of Southern California Edison, San Onofre Nuclear Generating Station (SONGS) 316(b) Demonstration, Final, June 22, 1994."  This report found compliance with 316(b) requirements under the condition of certain mitigation measures.  The report found adverse impacts to organisms in not only the cooling water system of the facility but also various biological populations or communities in the vicinity of the intake/discharge locations for the station.  These effects included mortality for fish, especially eggs and larvae, that are taken into the station with the cooling water, and creating a sometimes turbid plume that affects the kelp, fish, and invertebrates in the San Onofre kelp bed.  Mitigation measures recommended by the SAIC report include installation of a fish guidance system, wetland restoration, kelp restoration, turbidity monitoring, and fish return system performance monitoring.

66.Compliance with Section 316(b) for issuance of an NPDES discharge permit for SONGS units 2 and 3 shall be conditional as specified in Provision E.18 of this Order.

67.On July 10, 1984, SCE submitted an initial request for a Clean Water Act Section 301(g) environmental quality variance to the Regional Board.  On January 23, 1985, SCE made final application for a Clean Water Act Section 301(g) environmental quality variance.  SCE requested a variance from 40 CFR Part 423.13 which limits the concentration of total residual chlorine in discharged condenser cooling water to 0.2 mg/l.  On May 5, 1994, SCE withdrew its application for a Section 301(g) variance citing an ability to operate subject to the BAT guideline.

68.On November 19, 1991, the State Board adopted the General Industrial storm water Permit, Order No. 91-13-DWQ (as amended by Water Quality Order No. 92-12-DWQ), NPDES No. CAS000001.  On November 4, 1992, SCE submitted a Notice of Intent to the State Board for obtaining coverage of the SONGS facilities under Order No. 91-13-DWQ.  The State Board confirmed coverage of the SONGS facilities under Order No. 91-13-DWQ and assigned WDID# 9 375003198 to the facilities.  On June 10, 1997, SCE submitted a second Notice of Intent for coverage under the newly adopted State General Stormwater Permit Order No. 97-03-DWQ.  Coverage continued automatically using the same WDID as was previously assigned.

69.The Federal Nuclear Regulatory Commission is responsible for the regulation of SONGS Unit 2 with respect to radiological material.  The Regional Board has no jurisdiction over regulation of radiological material or the discharge of radiological wastes from SONGS Unit 2.

70.Water Quality impacts of discharges from SONGS Unit 2 are consistent with maximum benefit to the people of the State and do not unreasonably affect present and anticipated beneficial use of ocean waters.  Also, there is not convincing evidence that the discharges result in water quality less than that prescribed in applicable plans and policies as described in this Order.  Therefore, discharges from SONGS Unit 2 as described in this Order are consistent with State Board Resolution No. 68-16, "Statement of Policy with Respect to Maintaining High Quality Waters in California."

71.The Regional Board, in establishing the requirements contained herein, considered factors including, but not limited to, the following:

a.	Past, present, and probable future beneficial uses of the ocean waters under consideration;

b.	Environmental characteristics of the ocean waters under consideration, including the quality of the water available thereto;

c.	Water quality conditions that could reasonably be achieved through the coordinated control of all factors that affect water quality in the area;

d.	Economic considerations;

e.	The need for developing housing within the region;

f.	The need to develop and use recycled water;

g.	Beneficial uses to be protected and water quality objectives reasonably required for that purpose;

h.	Other waste discharges; and,

i.	The need to prevent nuisance.

72.The Regional Board has considered all water resource related environmental factors associated with the SONGS Unit 2 discharge.

73.The Regional Board has notified SCE and all known interested parties of its intent to prescribe waste discharge requirements for the discharge.

74.The Regional Board has, in a public meeting, heard and considered all comments pertaining to the discharge.

75.This Order shall serve as a National Pollutant Discharge Elimination System Permit pursuant to Section 402 of the federal Clean Water Act or amendments thereto.

76.The issuance of waste discharge requirements for this discharge is exempt from the provisions of the California Environmental Quality Act (Chapter 3, Section 21000 et seq of Division 13 of the Public Resources Code) in accordance with Water Code Section 13389.

77.Metal Cleaning waste streams include the following:

- Chemical Metal Cleaning wastes

- Non-Chemical Metal Cleaning wastes

The metal cleaning waste streams identified above are described in finding Nos. 78 and 79.

78.Chemical metal cleaning wastes result from steam generator cleaning that is performed under outage conditions.  Discharges occur intermittently with a total volume of approximately 750,000 gallons of wastewater per unit.  About one-third of this volume is treated steam generator cleaning solution.  The remainder consists of post-cleaning rinsate.

79.Non-chemical metal cleaning consists of or contains particulate debris from the steam generators and feedwater piping.  This generally occurs during fuel outages.  The waste water from the non-chemical metal cleaning process will be routed through diatomaceous earth and cartridge filters for treatment prior to discharge to the Full Flow Condensate Polishing Regenerant waste stream, a low volume in-plant waste.  Discharge of this waste averages 0.040 MGD.

IT IS HEREBY ORDERED, that the Southern California Edison Company (hereinafter Discharger), in order to meet the provisions contained in Division 7 of the California Water Code and regulations adopted thereunder and the provisions of the Clean Water Act and regulations adopted thereunder, shall comply with the following requirements for the discharge through the SONGS Unit 2 Outfall, the Units 2 and 3 Fish Return System Outfall, and for all Across-the-Beach discharges.

A. PROHIBITIONS

1.	Compliance with the waste discharge prohibitions contained in the Basin Plan and listed in Attachment F hereto is required as a condition of this Order.

2.	Discharges of waste in a manner or to a location which have 	not been specifically described to the Regional Board and for 	which valid waste discharge requirements are not in force are 	prohibited.

3.	The discharge of oil or any residuary product of petroleum to 	the waters of the State, except in accord with waste discharge 	requirements or other provisions of Division 7, California 	Water Code is prohibited.

4.	The discharge of any radiological, chemical, or biological 	warfare agent is prohibited.

5.	The discharge of polychlorinated biphenyl compounds, such as 	those commonly used for transformer fluid, is prohibited.

6.	The discharge of municipal and industrial waste sludge 	directly to the ocean, or into a waste stream that discharges 	to the ocean is prohibited.  The discharge of sludge digester 	supernatant directly to the ocean, or to a waste stream that 	discharges to the ocean without further treatment, is 	prohibited.

7.	The bypassing of untreated wastes containing concentrations of 	pollutants in excess of those of Table A or Table B of the 	Ocean Plan to the ocean is prohibited except under those 	circumstances described under Provision E.17 of this Order.

8.	The discharge through the SONGS Unit 2 Outfall in excess of 	1286.9 MGD is prohibited unless the Discharger obtains revised 	waste discharge requirements for the proposed increased 	discharge flowrate.

9.	Total residual oxidants may not be discharged from any single 	generating unit for more than two hours per day unless the 	Discharger demonstrates to the Regional Board Executive 	Officer that discharge for more than two hours is required for 	macroinvertebrate control.  Simultaneous multi-unit 	chlorination/bromination is permitted.

B. DISCHARGE SPECIFICATIONS

1.	The combined discharge through the SONGS Unit 2 Outfall to the 	Pacific Ocean containing pollutants in excess of the following 	effluent limitations is prohibited.1/2/3/

| Parameter | Units | 6-Month Median4/ | Daily Maximum5/ | Instantaneous Maximum6/ |
| --- | --- | --- | --- | --- |
| Arsenic | ug/l lb/day | 58 620 | 320 3500 | 850 9100 |
| Cadmium | ug/l lb/day | 11 120 | 44 470 | 110 1200 |
| Chromium (Hexavalent)7/ | ug/l lb/day | 22 240 | 88 940 | 220 2400 |
| Copper | ug/l lb/day | 13 140 | 110 1200 | 310 3300 |
| Lead | ug/l lb/day | 22 240 | 88 940 | 220 2400 |
| Mercury | ug/l lb/day | 0.44 4.7 | 1.8 19 | 4.4 47 |
| Nickel | ug/l lb/day | 55 590 | 220 2400 | 550 5900 |
| Selenium | ug/l lb/day | 170 1800 | 660 7100 | 1700 18000 |
| Silver | ug/l lb/day | 6.1 65 | 29 310 | 75 810 |
| Zinc | ug/l lb/day | 140 1500 | 800 8600 | 2100 23000 |
| Cyanide | ug/l lb/day | 11 120 | 44 470 | 110 1200 |
| Total Chlorine Residual8/ | ug/l lb/day | 22 240 | 88 940 | 200 2100 |
| Ammonia (as N) | ug/l lb/day | 5200 56000 | 25000 270000 | 65000 690000 |
| Phenolic Compounds (non- Chlorinated) | ug/l lb/day | 290 3100 | 1300 14000 | 3300 35000 |
| Chlorinated Phenolics | ug/l lb/day | 11 120 | 44 470 | 110 1200 |
| Endosulfan | ug/l lb/day | 0.1 1.1 | 0.2 2.1 | 0.3 3.2 |
| Endrin | ug/l lb/day | 0.022 0.24 | 0.044 0.47 | 0.066 0.71 |
| HCH9/ | ug/l lb/day | 0.044 0.47 | 0.088 0.94 | 0.13 1.4 |

Note:	ug/l = micrograms per liter

lb/day = pounds per day

| Parameter | Units | 30-day Average |
| --- | --- | --- |
| Acrolein | ug/l lb/day | 2,400 26,000 |
| Antimony | ug/l lb/day | 13,000 140,000 |
| bis(2-chloroethoxy) methane | ug/l lb/day | 48 520 |
| bis(2-chloroisopropyl) ether | ug/l lb/day | 13,000 140,000 |
| Chlorobenzene | ug/l lb/day | 6,300 67,000 |
| Chromium (III) | ug/l lb/day | 2,100,000 22,000,000 |
| di-n-butyl phthalate | ug/l lb/day | 39,000 410,000 |
| Dichlorobenzenes9/ | ug/l lb/day | 56,000 600,000 |
| 1,1-dichloroethylene | ug/l lb/day | 78,000 840,000 |
| Diethyl phthalate | ug/l lb/day | 360,000 3,900,000 |
| Dimethyl phthalate | ug/l lb/day | 9,000,000 97,000,000 |
| 4,6-dinitro-2-methylphenol | ug/l lb/day | 2,400 26,000 |
| 2,4-dinitrophenol | ug/l lb/day | 44 470 |
| Ethylbenzene | ug/l lb/day | 45,000 480,000 |
| Fluoranthene | ug/l lb/day | 170 1,800 |
| Hexachlorocyclopentadiene | ug/l lb/day | 640 6,800 |
| Isophorone | ug/l lb/day | 1,700,000 18,000,000 |
| Nitrobenzene | ug/l lb/day | 54 580 |
| Thallium | ug/l lb/day | 150 1,700 |
| Toluene | ug/l lb/day | 940,000 10,000,000 |
| 1,1,2,2-tetrachloroethane | ug/l lb/day | 13,000 140,000 |
| Tributyltin | ug/l lb/day | 0.015 0.17 |
| 1,1,1-trichloroethane | ug/l lb/day | 5,900,000 64,000,000 |
| 1,1,2-trichloroethane | ug/l lb/day | 470,000 5,100,000 |
| Acrylonitrile | ug/l lb/day | 1.1 12 |
| Aldrin | ug/l lb/day | 0.00024 0.0026 |
| Benzene | ug/l lb/day | 65 700 |
| Benzidine | ug/l lb/day | 0.00076 0.0081 |
| Beryllium | ug/l lb/day | 0.36 3.9 |
| bis(2-chloroethyl) ether | ug/l lb/day | 0.5 5.3 |
| bis(2-ethylhexyl) phthalate | ug/l lb/day | 39 410 |
| Carbon tetrachloride | ug/l lb/day | 9.9 110 |
| Chlordane9/ | ug/l lb/day | 0.00025 0.0027 |
| Chloroform | ug/l lb/day | 1,400 15,000 |
| DDT9/ | ug/l lb/day | 0.0019 0.02 |
| 1,4-dichlorobenzene | ug/l lb/day | 200 2,100 |
| 3,3-dichlorobenzidine | ug/l lb/day | 0.089 0.96 |
| 1,2-dichloroethane | ug/l lb/day | 1,400 15,000 |
| Dichloromethane | ug/l lb/day | 5,000 53,000 |
| 1,3-dichloropropene | ug/l lb/day | 98 1,100 |
| Dieldrin | ug/l lb/day | 0.00044 0.0047 |
| 2,4-dinitrotoluene | ug/l lb/day | 29 310 |
| 1,2-diphenylhydrazine | ug/l lb/day | 1.8 19 |
| Halomethanes9/ | ug/l lb/day | 1,400 15,000 |
| Heptachlor9/ | ug/l lb/day | 0.0079 0.085 |
| Hexachlorobenzene | ug/l lb/day | 0.0023 0.025 |
| Hexachlorobutadiene | ug/l lb/day | 150 1,700 |
| Hexachloroethane | ug/l lb/day | 28 300 |
| N-nitrosodimethylamine | ug/l lb/day | 80 860 |
| N-nitrosodiphenylamine | ug/l lb/day | 28 300 |
| PAHs9/ | ug/l lb/day | 0.097 1.0 |
| PCBs9/ | ug/l lb/day | 0.0002.1 0.0021 |
| TCDD equivalents9/ | ug/l lb/day | 0.000000043 0.00000046 |
| Tetrachloroethylene | ug/l lb/day | 1,100 12,000 |
| Toxaphene | ug/l lb/day | 0.0023 0.02.5 |
| Trichloroethylene | ug/l lb/day | 300 3,200 |
| 2,4,6-trichlorophenol | ug/l lb/day | 3.2 34 |
| Vinyl chloride | ug/l lb/day | 400 4,300 |

Note:	ug/l = micrograms per liter

lb/day = pounds per day

| Parameter | Units | Monthly Average10/ | Weekly Average11/ | Daily Maximum5/ | Maximum at any time |
| --- | --- | --- | --- | --- | --- |
| Acute Toxicity12/ | TUa | 1.5 | 2.0 | -- | 2.5 |
| Chronic Toxicity12/ | TUc | -- | -- | 10 | -- |

2.	Waste discharged9/ through the SONGS Unit 2 Outfall to the ocean9/ shall be essentially free of:

a.	Material that is floatable or will become floatable upon 	discharge;

b.	Settleable material or substances that may form sediments 	which will degrade9/ benthic communities or other aquatic 	life;

c.	Substances which will accumulate to toxic levels in marine 	waters, sediments or biota;

d.	Substances that significantly9/ decrease the natural9/ 	light to benthic communities and other marine life; and

e.	Materials that result in aesthetically undesirable 				discoloration of the ocean9/ surface.

3.	Songs Unit 2 waste9/ management systems that discharge to the 	ocean9/ shall be designed and operated in a manner that will 	maintain the indigenous marine life and a healthy and diverse 	marine community

4.	Waste9/ effluents from SONGS Unit 2 shall be discharged to the 	ocean in a manner that provides sufficient initial9/ dilution 	to minimize the concentrations of pollutants and ensure 	compliance with water quality objectives.

- The location of the waste9/ discharge from SONGS Unit 2 shall 	assure that:

a.	Pathogenic organisms and viruses are not present in ares of 		where shellfish9/ are harvested for human consumption or in 		areas used for swimming or other body contact sports:

b.	Natural water quality conditions are not altered in areas 		designated as being of special biological significance or 		areas that existing marine laboratories use as a source of 		seawater; and

c.	Maximum protection is provided to the marine environment.

6.	Waste9/ that contains pathogenic organisms or viruses should 	be discharged a sufficient distance from shellfishing9/ and 	water-contact sports areas to maintain applicable 	bacteriological standards without disinfection.  Where 	conditions are such that an adequate distance cannot be 	attained, reliable disinfection in conjunction with a 	reasonable separation of the discharge point from the area of 	use must be provided.  Disinfection procedures that do not 	increase effluent toxicity and that constitute the least 	environmental and human hazard should be used.

7. The SONGS Unit 2 discharge of elevated temperature wastes to 	the ocean shall comply with limitations necessary to assure 	protection of beneficial uses and designated areas of special 	biological significance.

8.	At all times except during heat treatment operations, the 	maximum temperature of the discharge from SONGS Unit 2 to the 	ocean shall not exceed the natural temperature of receiving 	waters by more than 25F.

9.	The pH of the discharge from SONGS Unit 2 to the ocean shall 	be within the limits of 6.0 to 9.0 pH units at all times.

10.The discharge from the thermophilic digester (a low volume 	waste) to the SONGS Unit 2 combined discharge outfall 	containing pollutants in excess of the following effluent 	limitations is prohibited: (based on a maximum flowrate of 	0.010 MGD)13/

| Parameter | Units2/ | Monthly Average10/ | Daily Maximum5/ | Instantaneous Maximum6/ |
| --- | --- | --- | --- | --- |
| Total Suspended Solids | mg/l lb/day | 30.0 2.5 | 100.0 8.3 | 100.0 8.3 |
| Grease and Oil | mg/l lb/day | 15.0 1.3 | 20.0 1.7 | 20.0 1.7 |

11.The discharge of condenser hotwell overboard (a low volume 	waste) to the SONGS Unit 2 combined discharge outfall 	containing pollutants in excess of the following effluent 	limitations is prohibited:  (based on a maximum flowrate of 	7.20 MGD)13/

| Parameter | Units2/ | Monthly Average10/ | Daily Maximum5/ | Instantaneous Maximum6/ |
| --- | --- | --- | --- | --- |
| Total Suspended Solids | mg/l lb/day | 30.0 1,800 | 100.0 6,000 | 100.0 6,000 |
| Grease and Oil | mg/l lb/day | 15.0 900 | 20.0 1,200 | 20.0 1,200 |

12.The discharge of steam generator blowdown (a low volume waste) 	to the SONGS Unit 2 combined discharge outfall containing 	pollutants in excess of the following effluent limitations is 	prohibited: (based on a 0.720 MGD)13/

| Parameter | Units2/ | Monthly Average10/ | Daily Maximum5/ | Instantaneous Maximum6/ |
| --- | --- | --- | --- | --- |
| Total Suspended Solids | mg/l lb/day | 30.0 180 | 100.0 600 | 100.0 600 |
| Grease and Oil | mg/l lb/day | 15.0 90 | 20.0 120 | 20.0 120 |

13.The discharge of blowdown processing system demineralizer 	regenerants (a low volume waste) to the SONGS Unit 2 combined 	discharge outfall containing pollutants in excess of the 	following effluent limitations is prohibited: (based on a 	maximum flowrate of 0.085 MGD)13/

| Parameter | Units2/ | Monthly Average10/ | Daily Maximum5/ | Instantaneous Maximum6/ |
| --- | --- | --- | --- | --- |
| Total Suspended Solids | mg/l lb/day | 30.0 21 | 100.0 71 | 100.0 71 |
| Grease and Oil | mg/l lb/day | 15.0 11 | 20.0 14 | 20.0 14 |

14.The discharge of full flow condensate polishing demineralizer 	regenerants (a low volume waste) to the SONGS Unit 2 combined 	discharge outfall containing pollutants in excess of the 	following effluent limitations is prohibited:  (based on a 	maximum flowrate of 1.40 MGD)13/

| Parameter | Units2/ | Monthly Average10/ | Daily Maximum5/ | Instantaneous Maximum6/ |
| --- | --- | --- | --- | --- |
| Total Suspended Solids | mg/l lb/day | 30.0 350 | 100.0 1200 | 100.0 1200 |
| Grease and Oil | mg/l lb/day | 15.0 180 | 20.0 230 | 20.0 230 |

15.The discharge of makeup demineralizer regenerants (a low 	volume waste) to the SONGS Unit 2 combined discharge outfall 	containing pollutants in excess of the following effluent 	limitations is prohibited: (based on a maximum flowrate of 	0.670 MGD)13/

| Parameter | Units2/ | Monthly Average10/ | Daily Maximum5/ | Instantaneous Maximum6/ |
| --- | --- | --- | --- | --- |
| Total Suspended Solids | mg/l lb/day | 30.0 170 | 100.0 560 | 100.0 560 |
| Grease and Oil | mg/l lb/day | 15.0 84 | 20.0 110 | 20.0 110 |

16.The discharge from the radwaste system (a low volume waste) to 	the SONGS Unit 2 combined discharge outfall containing 	pollutants in excess of the following effluent limitations is 	prohibited: (based on a maximum flowrate of 0.432 MGD)13/

| Parameter | Units2/ | Monthly Average10/ | Daily Maximum5/ | Instantaneous Maximum6/ |
| --- | --- | --- | --- | --- |
| Total Suspended Solids | mg/l lb/day | 30.0 110 | 100.0 360 | 100.0 360 |
| Grease and Oil | mg/l lb/day | 15.0 54 | 20.0 72 | 20.0 72 |

17.The discharge from building sumps (a low volume waste) to the 	SONGS Unit 2 combined discharge outfall containing pollutants 	in excess of the following effluent limitations is prohibited: 	(based on a maximum flowrate of 0.800 MGD)13/

| Parameter | Units2/ | Monthly Average10/ | Daily Maximum5/ | Instantaneous Maximum6/ |
| --- | --- | --- | --- | --- |
| Total Suspended Solids | mg/l lb/day | 30.0 200 | 100.0 670 | 100.0 670 |
| Grease and Oil | mg/l lb/day | 15.0 100 | 20.0 130 | 20.0 130 |

18.The discharge from the intake structure sump (a low volume 	waste) to the SONGS Unit 2 combined discharge outfall 	containing pollutants in excess of the following effluent 	limitations is prohibited: (based on a maximum flowrate of 	0.288 MGD)13/

| Parameter | Units2/ | Monthly Average10/ | Daily Maximum5/ | Instantaneous Maximum6/ |
| --- | --- | --- | --- | --- |
| Total Suspended Solids | mg/l lb/day | 30.0 72 | 100.0 240 | 100.0 240 |
| Grease and Oil | mg/l lb/day | 15.0 36 | 20.0 48 | 20.0 48 |

19.The combined discharge from all SONGS Unit 2 low volume waste 	sources, taken together, containing pollutants in excess of 	the following effluent limitations is prohibited: (based on a 	maximum flowrate of 11.61 MGD)13/

| Parameter | Units2/ | Monthly Average10/ | Daily Maximum5/ | Instantaneous Maximum6/ |
| --- | --- | --- | --- | --- |
| Total Suspended Solids | mg/l lb/day | 30.0 2,900 | 100.0 9,700 | 100.0 9,700 |
| Grease and Oil | mg/l lb/day | 15.0 1,500 | 20.0 1,900 | 20.0 1,900 |

20.The discharge from the SONGS Unit 1 sewage treatment plant 	shall not exceed the following effluent limitations: (based on 	a maximum flowrate of 0.10 MGD)14/

| Parameter | Units2/ | 30-Day Average10/ | 7-Day Average11/ | Maximum at any time |  |
| --- | --- | --- | --- | --- | --- |
| Grease and Oil | mg/l lb/day | 25 21 | 40 33 | 75 63 |  |
| Total Suspended Solids | mg/l | Not more than 25% of influent total suspended solids |  |  |  |
| Settleable Solids | ml/l | 1.0 | 1.5 | 3.0 |  |
| Turbidity | NTU | 75 | 100 | 225 |  |
| PH | pH units | Within the limits of 6.0 to 9.0 at all times |  |  |  |  |
| Acute Toxicity12/ | TUa | 1.5 | 2.0 | 2.5 |  |

Note: ml/l = milliliters per liter

NTU = Nephelometric turbidity units

21.The discharge from the Mesa Facility Complex sewage treatment 	plant shall not exceed the following effluent limitations: 	(based on a maximum flowrate of 0.045 MGD)15/

| Parameter | Units2/ | 30-Day Average10/ | 7-Day Average11/ | Maximum at any time |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Grease and Oil | mg/l lb/day | 25 21 | 40 33 | 75 63 |  |  |  |
| Total Suspended Solids | mg/l | Not more than 25% of influent total suspended solids |  |  |  |  |  |
| Settleable Solids | ml/l | 1.0 | 1.5 | 3.0 |  |  |  |
| Turbidity | NTU | 75 | 100 | 225 |  |  |  |
| pH | pH units | Within the limits of 6.0 to 9.0 at all times |  |  |  |  |  |  |  |
| Acute Toxicity12/ | TUa | 1.5 | 2.0 | 2.5 |  |  |  |

Note: ml/l = milliliters per liter

NTU = Nephelometric turbidity units

22.The discharge through the SONGS Units 2 and 3 Fish Return 	System Outfall and any Across-the-Beach discharge containing 	pollutants in excess of effluent limitations equal to the 	toxic material limitations contained in Receiving Water 	Limitation D.3 of this Order is prohibited.

23.The discharge of substances for which effluent limits are not 	established by this Order shall be prevented or, if the 	discharge cannot be prevented, minimized.

24.The discharge of metal cleaning wastes from the steam 	generator cleaning process at SONGS to the Pacific Ocean 	containing pollutants in excess of the following effluent 	limitations is prohibited:

The Quantity of pollutants discharged in metal cleaning wastes 	shall not exceed the quantity determined by multiplying the 	flow of metal cleaning wastes times the concentration listed 	in the following table:

| Parameter | Units | 30-day Average | Daily Maximum | Instantaneous Maximum |
| --- | --- | --- | --- | --- |
| Total suspended solids | mg/l | 30.0 | 100.0 | BPT* |
| Oil & Grease | mg/l | 15.0 | 20.0 | BPT* |
| Copper, total | mg/l | 1.0 | 1.0 | BPT* |
| Iron, total | mg/l | 1.0 | 1.0 | BPT* |

*BPT = Best practicable control technology (40CFR Part 423.12(b)(5))

25.The discharge of non-chemical metal cleaning waste from this 	facility to the combined discharge outfall containing 	pollutants in excess of the following effluent limitation is 	prohibited:  (based on a maximum flowrate of 0.040 MGD)

The quantity of pollutants discharged in non-chemical metal 	cleaning wastes shall not exceed the quantity determined by 	multiplying the flow of non-chemical metal cleaning wastes 	times the concentration listed in the following table.

| Parameter | Units | 30-day Average | Daily Maximum | Instantaneous Maximum |
| --- | --- | --- | --- | --- |
| Total suspended solids | mg/l | 30.0 | 100.0 | BPT* |
| Oil & Grease | mg/l | 15.0 | 20.0 | BPT* |
| Copper, total | mg/l | 1.0 | 1.0 | BPT* |
| Iron, total | mg/l | 1.0 | 1.0 | BPT* |

*BPT = Best practicable control technology (40CFR Part 423.12(b)(5))

C.	HEAT TREATMENT DISCHARGE SPECIFICATIONS

The Discharger may raise the temperature in excess of the temperature of the cooling water discharge to the Pacific Ocean in excess of the temperature specified in Discharge Specification B.7 during periods of heat treatment in accordance with the following specifications:

1.	The frequency of heat treatment shall be determined, in part, 	by a growth model for the Bay Mussel, Mytilus edulis, as 	described in Attachment D.  Measurements and observations of 	biological material from the conduit and observation of 	cooling water system parameters shall also be used.  System 	operational constraints may require that a heat treatment be 	conducted prior to the time scheduled using the parameters 	above, typically during the prior weekend.

2.	Heat treatment temperature and duration shall be based on the Time-Temperature Mortality Curve for the Bay Mussel, Mytilus Edulis (Attachment E), which includes an additional amount of time added to account for temperature measurement inaccuracy, non-homogeneity of temperature in the cooling water system, and other unknown factors.  The highest temperature consistent with plant operating requirements shall be selected to keep the heat treatment time to a minimum.  Target times shall be rounded up to the nearest five minutes.

3.	The target temperature and time is subject to the precision 	that can be practicably attained by station operators.  	Consequently, during the temperature rise period, before 	initiating heat treatment, and as the influent temperature 	varies, temperatures may be inadvertently increased above the 	target temperature due to equipment limitations; however, the 	target temperature shall not be exceeded by more than 10F or 	more than fifteen (15) minutes.

4.	Heat treatment of the intake conduit, fish return system and 	screenwell shall be performed at 100F (as measured in the 	screenwell) for 2.1 hours.  100F represents the presently 	expected, maximum temperature capability of each unit. The 	heat 	treatment temperature will be adjusted upward or 	downward to the highest temperature compatible with station 	operation during initial operation of the units.  A 	corresponding change shall be made to the heat treatment 	duration in accordance with the Bay Mussel Time-Temperature 	Mortality Curve (Attachment E).  (Heat treatment duration 	represents the period of time at the target temperature, and 	not the time required to reach 100F, nor the time to return 	to normal operation).

5.	Heat treatment of the intake conduit, fish return system and 	screenwell shall be conducted at intervals predicted by a 	growth model, which is based on ambient water temperature.  	Heat treatments shall be scheduled using the SONGS Units 2 and 	3 heat treatment Decision Flow Chart (Attachment D).  Heat 	treatments may also be conducted prior to or following a 	station outage, if the outage period is anticipated to extend 	beyond the time of the next (growth model) predicted heat 		treatment.

6.	As long as normal operating discharge temperatures exceed 80F 	for a minimum of 1000 hours, 85F for 150 hours or 90F for 31 	hours, the discharge conduit will not require heat treatment.  	Unless these conditions are met, it must be assumed that 	settling and growth of biofouling organisms has occurred.  	When these conditions are not met, growth calculations, based 	on ambient intake water temperatures, shall be used to 	schedule a discharge conduit heat treatment.

7.	When required, the discharge conduit for Unit 2 may be heat 	treated at a discharge temperature of 105F for 1.1 hours.  		This time is the onshore heat treatment time required to treat 	the furthest point offshore for 0.58 hours, the time indicated 	by the Time-Temperature Mortality Curve for the Bay Mussel 	(Attachment E).

8. During heat treatment, heat added to the cooling water shall 	not cause the temperature of the discharge from the intake 	conduit to the Pacific Ocean to exceed 125F, except as 	specified in Heat Treatment Discharge Specification No. C.3.

9.	During heat treatment, heat added to the cooling water shall 	not cause the temperature of the discharge from ths discharge 	conduit to the Pacific Ocean to exceed 105F, except as 	specified in Heat Treatment Discharge Specification No. C.3.  	During Unit 3 heat treatments, the difference between intake 	and discharge water temperatures for Unit 2 may exceed 25F 	due to crossover connections with Unit 3.

D.	RECEIVING WATER LIMITATIONS

1.	The SONGS Unit 2 discharge to the Pacific Ocean shall not by 	itself or jointly with any discharge or discharges cause the 	following Thermal Plan ocean water quality objective to be 	violated:

Thermal Characteristics

The discharges of elevated temperature wastes shall not 			result in increases in the natural water temperature 				exceeding 4F at (a) the shoreline, (b) the surface of any 		ocean substrate, or (c) the ocean surface beyond 1,000 feet 		from the discharge system.  The surface temperature 				limitation shall be maintained at least 50 percent of the 		limitation of any complete tidal cycle.

2.	The SONGS Unit 2 discharge to the Pacific Ocean shall not by 	itself or jointly with any other discharge or discharges cause 	the following Ocean Plan water quality objectives to be 	violated.  Compliance with these objectives shall be 	determined from samples collected at stations representative 	of the area within the waste field where initial9/ dilution is 	completed.

a.	Bacterial Characteristics

(1)Within a zone bounded by the shoreline and a distance of 			1,000 feet from the shoreline or the 30-foot depth 				contour, whichever is further from the shoreline, and in 			areas outside this zone used for water contact sports, 			as determined by the Regional Board, but including all 			kelp9/ beds, the following bacterial objectives shall be 			maintained throughout the water column:

(a)Samples of water from each sampling station shall 					have a density of total coliform organisms less than 				1,000 per 100 ml (10 per ml); provided that not more 				than 20 percent of the samples at any sampling 						station, in any 30-day period, may exceed 1,000 per 				100 ml (10 per ml), and provided further that no 					single sample when verified by a repeat sample taken 				within 48 hours shall exceed 10,000 per 100 ml (100 				per ml).

(b)The fecal coliform density, based on a minimum of not 				less than five samples for any 30-day period, shall 				not exceed a geometric mean of 200 per 100 ml nor 					shall more than 10 percent of the total samples 					during any 60-day period exceed 400 per 100 ml.

The "Initial Dilution Zone" of wastewater outfalls shall be excluded from designation as "kelp beds" for purposes of bacterial standards, and Regional Boards should recommend extension of such exclusion zone where warranted to the SWRCB (for consideration under Chapter VI.F.).  Adventitious assemblages of kelp plants on waste discharge structures (e.g., outfall pipes and diffusers) do not constitute kelp beds for purposes of bacterial standards

(2)At all areas where shellfish9/ may be harvested for 				human consumption, as determined by the Regional Board, 			the following bacterial objectives shall be maintained 			throughout the water column:

The median total coliform density shall not exceed 70 			per 100 ml, and not more than 10 percent of the samples 			shall exceed 230 per 100 ml.

b.	Physical Characteristics

(1)Floating particulates and grease and oil shall not be 			visible.

(2)The discharge of waste9/ shall not cause aesthetically 			undesirable discoloration of the ocean9/ surface.

(3)Natural9/ light shall not be significantly9/ reduced at 			any point outside the initial dilution zone as the 				result of the discharge of waste.

(4)The rate of deposition of inert solids and the 						characteristics of inert solids ocean9/ sediments shall 			not be changed such that benthic communities are 					degraded9/.

c.	Chemical Characteristics

(1)The dissolved oxygen concentration shall not at any time 			be depressed more than 10 percent from that which occurs 			naturally, as the result of the discharge of oxygen 				demanding waste9/ materials.

(2)The pH shall not be changed at any time more than 0.2 			units from that which occurs naturally.

(3)The dissolved sulfide concentration of waters in and 				near sediments shall not be significantly9/ increased 				above that present under natural conditions.

(4)The concentration of substances set forth in Chapter IV, 			Table B, of the Ocean Plan in marine sediments shall not 			be increased to levels that would degrade9/ indigenous 			biota.

(5)The concentration of organic materials in marine 					sediments shall not be increased to levels that would 			degrade9/ marine life.

(6)Nutrient materials shall not cause objectionable aquatic 			growths or degrade9/ indigenous biota.

d.	Biological Characteristics

(1)Marine communities, including vertebrate, invertebrate, 			and plant species, shall not be degraded9/.

(2)The natural taste, odor, and color of fish, shellfish9/, 			or other marine resources used for human consumption 				shall not be altered.

(3)The concentration of organic materials in fish, 					shellfish9/, or other marine resources used for human 				consumption shall not bioaccumulate to levels that are 			harmful to human health.

3.	The SONGS Unit 2 discharge to the Pacific ocean shall not by 	itself or jointly with any other discharge or discharges cause 	the following Ocean Plan toxic material limitations to be 	exceeded in ocean waters upon completion of initial9/ 	dilution:

| Parameter | Units | 6-Month Median | Daily Maximum | Instantaneous Maximum |
| --- | --- | --- | --- | --- |
| Arsenic | ug/l | 8 | 32 | 80 |
| Cadmium | ug/l | 1 | 4 | 10 |
| Chromium (Hexavalent)7/ | ug/l | 2 | 8 | 20 |
| Copper | ug/l | 3 | 12 | 30 |
| Lead | ug/l | 2 | 8 | 20 |
| Mercury | ug/l | 0.04 | 0.16 | 0.4 |
| Nickel | ug/l | 5 | 20 | 50 |
| Selenium | ug/l | 15 | 60 | 150 |
| Silver | ug/l | 0.7 | 2.8 | 7 |
| Zinc | ug/l | 20 | 80 | 200 |
| Cyanide | ug/l | 1 | 4 | 10 |
| Total Chlorine Residual8/ | ug/l | 2 | 8 | 60 |
| Ammonia (as N) | ug/l | 600 | 2400 | 6000 |
| Chronic Toxicity | TUc | -- | 1 | -- |
| Phenolic Compounds (non- chlorinated) | ug/l | 30 | 120 | 300 |
| Chlorinated Phenolics | ug/l | 1 | 4 | 10 |
| Endosulfan | ug/l | 0.009 | 0.018 | 0.027 |
| Endrin | ug/l | 0.002 | 0.004 | 0.006 |
| HCH9/ | ug/l | 0.004 | 0.008 | 0.012 |

| Parameter | Units | 30-day Average |
| --- | --- | --- |
| Acrolein | ug/l | 220 |
| Antimony | ug/l | 1,200 |
| bis(2-chloroethoxy) methane | ug/l | 4.4 |
| bis(2-chloroisopropyl) ether | ug/l | 1,200 |
| Chlorobenzene | ug/l | 570 |
| chromium (III) | ug/l | 190,000 |
| di-n-butyl phthalate | ug/l | 3,500 |
| Dichlorobenzenes9/ | ug/l | 5,100 |
| 1,1-dichloroethylene | ug/l | 7,100 |
| diethyl phthalate | ug/l | 33,000 |
| dimethyl phthalate | ug/l | 820,000 |
| 4,6-dinitro-2-methylphenol | ug/l | 220 |
| 2,4-dinitrophenol | ug/l | 4.0 |
| Ethylbenzene | ug/l | 4,100 |
| Fluoranthene | ug/l | 15 |
| Hexachlorocyclopentadiene | ug/l | 58 |
| Isophorone | ug/l | 150,000 |
| Nitrobenzene | ug/l | 4.9 |
| Thallium | ug/l | 14 |
| Toluene | ug/l | 85,000 |
| 1,1,2,2-tetrachloroethane | ug/l | 1,200 |
| Tributyltin | ug/l | 0.0014 |
| 1,1,1-trichloroethane | ug/l | 540,000 |
| 1,1,2-trichloroethane | ug/l | 43,000 |
| Acrylonitrile | ug/l | 0.10 |
| Aldrin | ug/l | 0.000022 |
| Benzene | ug/l | 5.9 |
| Benzidine | ug/l | 0.000069 |
| Beryllium | ug/l | 0.033 |
| bis(2-chloroethyl) ether | ug/l | 0.045 |
| bis(2-ethylhexyl) phthalate | ug/l | 3.5 |
| carbon tetrachloride | ug/l | 0.90 |
| chlordane9/ | ug/l | 0.000023 |
| Chloroform | ug/l | 130 |
| DDT9/ | ug/l | 0.00017 |
| 1,4-dichlorobenzene | ug/l | 18 |
| 3,3-dichlorobenzidine | ug/l | 0.0081 |
| 1,2-dichloroethane | ug/l | 130 |
| Dichloromethane | ug/l | 450 |
| 1,3-dichloropropene | ug/l | 8.9 |
| Dieldrin | ug/l | 0.00004 |
| 2,4-dinitrotoluene | ug/l | 2.6 |
| 1,2-diphenylhydrazine | ug/l | 0.16 |
| Halomethanes9/ | ug/l | 130 |
| heptachlor9/ | ug/l | 0.00072 |
| Hexachlorobenzene | ug/l | 0.00021 |
| Hexachlorobutadiene | ug/l | 14 |
| Hexachloroethane | ug/l | 2.5 |
| N-nitrosodimethylamine | ug/l | 7.3 |
| N-nitrosodiphenylamine | ug/l | 2.5 |
| PAHs9/ | ug/l | 0.0088 |
| PCBs9/ | ug/l | 0.000019 |
| TCDD equivalents9/ | ug/l | 0.0000000039 |
| Tetrachloroethylene | ug/l | 99 |
| Toxaphene | ug/l | 0.00021 |
| Trichloroethylene | ug/l | 27 |
| 2,4,6-trichlorophenol | ug/l | 0.29 |
| vinyl chloride | ug/l | 36 |

Note:	ug/l = micrograms per liter

E.	PROVISIONS

1.	The discharger must comply with all conditions of this permit.  	Any permit noncompliance constitutes a violation of the Clean 	Water Act and is grounds for enforcement action; for permit 	termination, revocation and reissuance, or modification; or 	denial of a permit renewal application.

2.	Neither the treatment nor the discharge of pollutants shall 	create a pollution, contamination, or nuisance as defined by 	Section 13050 of the California Water code.

3.	The Discharger must comply with all conditions of this Order.  	Any permit noncompliance constitutes a violation of the Clean 	Water Act and the California Water Code and is grounds for 	enforcement action; for permit termination, revocation and 	reissuance, or modification; or for denial of a Report of 	Waste Discharge submitted in application for permit 	modification or reissuance.

4.	The Discharger shall take all reasonable steps to minimize or 	correct any adverse impact on the environment resulting from 	noncompliance with this Order, including such accelerated or 	additional monitoring as may be necessary to determine the 	nature and impact of the noncomplying discharge.

5.	This Order may be modified, revoked, and released, or 	terminated for cause including, but not limited to, the 	following:

a.	Violation of any terms or conditions of this Order;

b.	Obtaining this Order by misrepresentation or failure to 			disclose fully all relevant facts, or;

c. A change in any condition that requires either a temporary 		or permanent reduction, or elimination of the authorized 		discharge.

The filing of a request by the Discharger for modification, 	revocation and reissuance, or termination of this Order does 	not stay the conditions of this Order.  Notification by the 	Discharger of planned changes or of anticipated noncompliance 	with this Order does not stay the conditions of this Order.

6.	In addition to any other grounds specified herein, this permit 	may be modified or revoked at any time if, on the basis of any 	data, the Executive Officer determines that continued 	discharges may cause unreasonable degradation of the marine 	environment.

7.	Notwithstanding Provision E.6 above, if a toxic effluent 	standard or prohibition (including any schedule of compliance 	specified in such effluent standard or prohibition) is 	established under Section 307(a) of the Clean Water Act for a 	toxic pollutant which is present in the discharge and such 	standard or prohibition is more stringent than any limitation 	for such pollutant in this Order, this Order may be modified 	or revoked and reissued to conform to the toxic effluent 	standard or prohibition and the Discharger so notified.

8.	This discharge shall not cause a violation of any applicable 	water quality standard for receiving waters adopted by the 	Regional Board or the State Board as required by the Clean 	Water Act and regulations adopted thereunder.  If more 	stringent applicable water quality standards are promulgated 	or approved pursuant to Section 303 of the Clean Water Act or 	amendments thereto, the Regional Board may modify this Order 	in accordance with the more stringent standards.

9.	The discharger shall comply with the effluent standards and 	prohibitions established under Section 307(a) of the Clean 	Water Act for toxic pollutants within the time provided in the 	regulations that establish those standards or prohibitions, 	even if this Order has not yet been modified to incorporate 	the requirement.

10.The Discharger shall take all reasonable steps in a timely 	manner as agreed upon by the Regional Board Executive Officer 	to identify the source(s) of toxicity through a Toxicity 	Identification Evaluation (TIE) and, if appropriate, a 	Toxicity Reduction Evaluation (TRE), if the results of the 	acute or chronic toxicity tests exceed the toxicity limits 	specified in Discharge Specification B.1 of this Order.

At a minimum, the TIE/TRE shall be conducted in accordance 	with the following:

a.	TIE/TRE Requirements for Acute and Chronic Toxicity

(1)In accordance with EPA acute and chronic manuals 					EPA/600/6-91/005F (Phase I), EPA/600/R-92/080 (Phase 				II), and EPA/600/R-92/081 (Phase III), the Discharger 			shall initiate a Toxicity Identification Evaluation 				(TIE) within fifteen (15) days of the exceedance to 				identify the causes of the toxicity;

(2)In accordance with EPA manual EPA/600/2-88/070, (TRE 				protocol for industrials) or any subsequent revisions, 			the Discharger shall initiate a Toxicity Reduction 				Evaluation (TRE) where appropriate; and

(3)Within (15) days of becoming aware of the violation, the 			Discharger shall submit to the Regional Board a report 			which specifies at least the following:

(a)the times and dates when the limitation was exceeded;

(b)the actions the Discharger has taken to mitigate the 				impact of the discharge to correct the exceedance and 				to prevent the recurrence of toxicity;

(c)the findings of TIE/TRE and any other investigations 				to identify the causes of the toxicity; and,

(d)if no TIE/TRE steps have been taken, the proposed 					schedule under which these actions will be 							implemented.

11.This order is not transferable to any person except after 	notice to the Regional Board Executive Officer.  The Regional 	Board may require modification or revocation and reissuance of 	this Order to change the name of the Discharger and 	incorporate such other requirements as may be necessary under 	the California Water Code and the Clean Water Act.  The 	Discharger shall submit notice of any transfer of this Order’s 	responsibility and coverage to a new discharger as described 	under Reporting Requirement F.3.

12.This Order does not convey any property rights of any sort or 	any exclusive privileges.  The requirements prescribed herein 	do not authorize the commission of any act causing injury to 	persons or property, nor protect the Discharger from 	liabilities under federal, state or local laws, nor create a 	vested right for the Discharger to continue the waste 	discharge.

13.The Discharger shall allow the Regional Board, or an 	authorized representative thereof, or any authorized 	representative of the United States Environmental Protection 	Agency, upon presentation of credentials and other documents 	as may be required by law, to:

a.	Enter upon the Discharger’s premises where a regulated 			facility or activity is located and conducted, or where 			records must be kept under the conditions of this Order;

b.	Have access to and copy, at reasonable times, any records 		that must be kept under the conditions of this Order;

c.	Inspect at reasonable times any facilities, equipment 			(including monitoring and control equipment), practices or 		operations regulated or required under this Order, and;

d.	Sample or monitor at reasonable times, for the purpose of 		assuring compliance with this Order or as otherwise 				authorized by the Clean Water Act or California Water Code, 		any substances or parameters at any location.

14.The Discharger shall, at all times, properly operate and 	maintain all facilities and systems or treatment and control 	(and related appurtenances) which are installed or used by the 	Discharger to achieve compliance with the conditions of this 	Order.  Proper operation and maintenance includes effective 	performance, adequate funding, adequate operator staffing and 	training, and adequate laboratory and process controls 	including appropriate quality assurance procedures.  This 	provision requires the operation of backup or auxiliary 	facilities or similar systems only when necessary to achieve 	compliance with the conditions of this Order.

15.In an enforcement action, it shall not be a defense for the 	Discharger that it would have been necessary to halt or reduce 	the permitted activity in order to maintain compliance with 	this Order.  Upon reduction, loss or failure of a treatment 	facility, the Discharger shall, to the extent necessary to 	maintain compliance with this Order, control production or all 	discharges, or both, until the facility is restored or an 	alternative method of treatment is provided.  This provision 	applies, for example, when the primary source of power of a 	treatment facility fails, is reduced or is lost.

16.Bypass of treatment facilities

a.	Definitions:

(1)"Bypass" means the intentional diversion of waste 					streams from any portion of a treatment facility.

(2)"Severe property damage" means substantial physical 				damage to property, damage to the treatment facilities 			which causes them to become inoperable, or substantial 			and permanent loss of natural resources which can be 				reasonably expected to occur in the absence of a bypass.  			Severe property damage does not mean economic loss 				caused by delays in production.

b.	Bypass Not Exceeding Effluent Limitations:

The Discharger may allow any bypass to occur which does not 		cause effluent limitations to be exceeded, but only if it 		is also for essential maintenance to assure efficient 			operation.  These bypasses are not subject to the 					provisions of paragraphs (c) and (d) of this provision.

c.	Notice of Anticipated Bypass and Unanticipated Bypass:

(1)Anticipated Bypass: If the Discharger knows that in advance of the need for a bypass, it shall submit prior notice, if possible, at least 10 days before the date of bypass.

(2)Unanticipated Bypass: The Discharger shall submit notice of the unanticipated bypass as described under Reporting Requirement F.4.

d.	Prohibition of Bypass:

(1)Bypass is prohibited and the Regional Board may take 				enforcement action against the Discharger for bypass 				unless:

(a)Bypass was unavoidable to prevent loss of life, 					personal injury, or severe property damage:

(b)There was no feasible alternative to the bypass, such 				as the use of auxiliary treatment facilities, 						retention of untreated wastes, or maintenance during 				normal periods of equipment downtime.  This condition 				is not satisfied if the Discharger could have 						installed adequate backup equipment to prevent a 					bypass which occurred during normal periods of 						equipment downtime or preventative maintenance; and

(c)The Discharger submitted notices as required under 				paragraph (c) of this section.

(2)The Executive Officer may approve an anticipated bypass, 			after considering its adverse effect if the Executive 			Officer determines that it will meet the three 						conditions listed above in paragraph (1) of this 					subsection.

17.Upset conditions

a.	Definition

"Upset" means an exceptional incident in which there is 			unintentional and temporary noncompliance with technology-		based effluent limitations because of factors beyond the 		reasonable control of the Discharger.  An upset does not 		include noncompliance to the extent caused by operational 		error, improperly designed treatment facilities, inadequate 		treatment facilities, lack of preventative maintenance, or 		careless or improper operation.

b.	Effect of an Upset

An upset constitutes an affirmative defense to an action 		brought for noncompliance with such technology-based permit 		effluent limitations if the requirements of paragraph (c) 		of this section are met.  No determination made during 			administrative review of claims that noncompliance was 			caused by upset, and before an action for noncompliance, is 		final administrative action subject to judicial review.

c.	Conditions Necessary for a Demonstration of Upset

A discharger who wishes to establish the affirmative 				defense of upset shall demonstrate, through properly 				signed, contemporaneous operating logs, or other relevant 		evidence that:

(1)An upset occurred and that the Discharger can identify 			the specific cause(s) of the upset;

(2)The permitted facility was at the time being properly 			operated; and

(3)The Discharger submitted notice of the upset as required 			in Reporting Requirement F.4.

d.	Burden of Proof

In any enforcement proceeding the Discharger seeking to 			establish the occurrence of an upset has the burden of 			proof.

18.In accordance with Section 316(b) of the Clean Water Act (33 	U.S.C. 1251 et seq.) the location, design, construction, and 	capacity of the SONGS unit 2 cooling water intake structure 	shall reflect the best technology available for minimizing 	adverse environmental impact.  The Discharger shall comply 	with any standards and guidelines that may be established by 	USEPA pursuant to Section 316(b) of the Clean Water Act.  The 	Discharger shall comply with the following conditions to 	demonstrate compliance with Clean Water Act Section 316(b):

a.	Continue use of effective techniques for reducing losses of 		midwater fishes in the intake structures, including (1) 			velocity caps on the intakes and (2) the Fish Return System 		(FRS).

b.	on July 16, 1991, the California Coastal Commission amended 		Permit No. 6-81-330-A (formerly Permit No. 183-73) to 			impose certain mitigation requirements upon SCE for impacts 		the Coastal Commission found to the marine environment 			caused by the operation of SONGS Units 2 and 3.  Compliance 		with the Coastal Commission permit is not under the 				authority of the Regional Board and is not required by this 		Order.  However, a failure to comply with the Coastal 			Commission permit mitigation requirement with regard to the 		FRS behavioral barriers described above may result in a 			reevaluation of the 316(b) adequacy finding.

c. The MRC (MRC 1989a) found that fish larvae are in greatest 		abundance in the coastal waters near SONGS during March and 		April.  The MRC predicts that a complete elimination of the 		water flow through SONGS during March and April could 			reduce the annual losses of fish larvae by 50%.  Where 			possible, the Regional Board encourages the Discharger to 		schedule all refueling and maintenance operations to occur 		during March and April, so as to maximize the savings in 		loss of fish larvae that would occur during these regularly 		scheduled periods of downtime.

19.The provisions of this Order are severable, and if any 	provisions of this Order, or the application of any provision 	of this Order to any circumstances, is held invalid, the 	application of such provision to other circumstances, and the 	remainder of this Order, shall not be affected thereby.

20.The Discharger shall have and implement a Best Management 	Practices (BMP) program in accordance with 40 CFR 125.100-104.  	The BMP program shall prevent, or minimize the 	potential for, 	the release of toxic or hazardous pollutants, including any 	such pollutants referred to in Finding No. 42, from ancillary 	activities to waters of the United States.  The Discharger 	shall maintain the BMP program in an up-to-date condition and 	shall amend the BMP program in accordance with 40 CFR 125.100-	125.104 whenever there is a change in facility design, 	construction, operation, or maintenance which materially 	affects the potential for discharge from SONGS Unit 2 of 	significant amounts of hazardous or toxic pollutants into 	waters of the United States.  The BMP program and any 	amendments thereto, shall be subject to the approval of the 	Executive Officer and shall be modified as directed by the 	Executive Officer.  The Discharger shall submit the BMP 	program and any amendments thereto to the Executive Officer 	upon request of the Executive Officer.  A copy of the up-to-	date BMP program shall be maintained at SONGS Unit 2 and shall 	be readily available to operating personnel at all times.

21.The Discharger shall comply with all requirements of the Standard Provisions (Attachments G and H) which are part of this Order.

F.	REPORTING REQUIREMENTS

1.	The Discharger shall file a new Report of Waste Discharge not 	less than 180 days prior to any material change or proposed 	change in the character, location, or volume of the discharge, 	including but not limited to, the following:

a.	Addition of a major industrial waste discharge to a 				discharge of essentially domestic sewage, or the addition 		of a new process or product by an industrial facility 			resulting in a change in the character of the waste.

b.	Significant change in disposal method, e.g., change from a 		land disposal to a direct discharge to water, or change in 		the method of treatment which would significantly alter the 		characteristics of the waste.

c. Significant change in the disposal area, e.g., moving the 		discharge to another drainage area, to a different water 		body, or to a disposal area significantly removed from the 		original area, potentially causing different water quality 		or nuisance problems.

d.	Increase in flow beyond that specified in this order.

2.	The Discharger shall give advance notice to the Executive 		Officer of any planned changes in the permitted facility or 	activity that may result in noncompliance with the 	requirements of this Order.

3. The Discharger shall notify the Executive Officer, in writing, 	at least 30 days in advance of any proposed transfer of this 	Order’s responsibility and coverage to a new discharger.  This 	notice must include a written agreement between the existing 	and new discharger containing a specific date for the transfer 	of this Order’s responsibility and coverage between the 	current discharger and the new discharger.  This agreement 	shall include an acknowledgement that the existing discharger 	is liable for violations up to the transfer date and that the 	new discharger is liable from the transfer date on.

4. The Discharger shall notify the Regional Board Executive 	Officer and the Long Beach and San Diego Offices of the 	California Department of Fish and Game, where practicable at 	least 48 hours in advance of any heat treatment at Unit 2.

5.	The Discharger shall report any noncompliance that may 	endanger health or the environment.  Any information shall be 	provided orally to the Executive Officer within 24 hours from 	the time the Discharger becomes aware of the circumstances.  A 	written submission shall also be provided within 5 days of the 	time the Discharger becomes aware of the circumstances.  The 	written submission shall contain a description of the 	noncompliance and its cause; the period of noncompliance, 	including exact dates and times, and if the noncompliance has 	not been corrected, the anticipated time it is expected to 	continue; and steps taken or planned to reduce, eliminate, and 	prevent recurrence of the noncompliance.  The Executive 	Officer or an authorized representative may waive the written 	report on a case-by-case basis if the oral report has been 	received within 24 hours.  The following shall be included as 	information that must be reported within 24 hours under this 	reporting requirement:

a.	Any unanticipated bypass which exceeds any effluent 				limitation of this Order.

b.	Any discharge of treated or untreated wastewater resulting 		from pipeline breaks, obstruction, surcharge or any other 		circumstances.

c.	Any upset which exceeds any effluent limitation in this 			Order.

d.	Any spills of polychlorinated biphenyl compounds (PCBs).  		The spill residue shall be drummed and disposed of in 			conformance with all applicable local state and federal 			regulations.  The written notification shall include 				pertinent information explaining the reasons for the spill 		and shall indicate what steps were taken to prevent the 			problem from recurring.

e.	Any violation of the prohibitions of this Order.

6.	The Discharger shall notify the Executive Officer as soon as 	they know or have reason to believe:

a.	That any activity has occurred or will occur which would 		result in a discharge, on a routine or frequent basis, 			of any toxic or non-toxic pollutant which is not limited in 		this Order, if that discharge will exceed the highest of 		the following "notification levels":

(1)One hundred micrograms per liter (100 ug/l);

(2)Two hundred micrograms per liter (200 ug/l) for 					acrolein and acrylonitrile; five hundred micrograms per 			liter (500 ug/l) for 2,4-dinitrophenol and for 2-methyl-			4,6-dinitrophenol; and one milligram per liter (1 mg/l) 			for antimony;

(3)Five (5) times the maximum concentration value reported 			for that toxic pollutant in the Report of Waste 					Discharge submitted in application for this order; or,

(4)The level established by the Regional Board in 						accordance with 40 CFR 122.44(f).

b.	That any activity has occurred or will occur which would 		result in any discharge, on a non-routine or infrequent 			basis, of a toxic or non-toxic pollutant which is not 			limited in the permit, if that discharge will exceed the 		highest of the following "notification levels":

(1)Five hundred micrograms per liter (500 ug/l);

(2)One milligram per liter (1 mg/l) for antimony;

(3)Ten (10) times the maximum concentration value reported 			for that pollutant in the Report of Waste Discharge 				submitted in application for this Order; or,

(4)The level established by the Regional Board in 						accordance with 40 CFR 122.44(f).

7.	The Discharger shall furnish to the Executive Officer within a 	reasonable time, any information that the Executive Officer 	may require to determine whether cause exists for modifying, 	revoking and reissuing, or terminating this Order.  The 	Discharger shall also furnish to the Executive Officer, upon 	request, copies of records required to be kept by this Order.

8.	Where the Discharger becomes aware that any relevant facts 	were not submitted in the permit application or that 	incorrect information was submitted in the permit application 	or in any report to the Regional Board, the Discharger shall 	promptly submit such facts or information.

9.	This Order expires on August 11, 2004.  If the Discharger 	wishes to continue any activity regulated by this Order after 	the expiration date of this Order, the Discharger must apply 	for and obtain new waste discharge requirements.  The 	Discharger must file a Report of Waste Discharge in accordance 	with Title 23, California Code of Regulations (CCR) and EPA 	forms 1 and 2C required by 40 Code of Federal Regulations 	(CFR) 122, not later than 180 days in advance of the 	expiration date of this order as application for issuance of 	new waste discharge requirements.

10.All applicants, reports, or information submitted to the 	Regional Board Executive officer shall be signed and 	certified.

a.	All Reports of Waste Discharge shall be signed as follows:

(1)For a corporation: by a responsible corporate officer.  			For the purpose of this section, a responsible corporate 			officer means: (i) A president, secretary, treasurer, or 			vice-president of the corporation in charge of a 					principal business function, or any other person who 				performs similar policy or decision-making functions for 			the corporation, or (ii) the manager of one of more 				manufacturing, production, or operating facilities 				employing more than 250 persons or having gross annual 			sales or expenditures exceeding $25 million (in second-			quarter 1980 dollars), if authority to sign documents 			has been assigned or delegated to the manager in 					accordance with corporate procedures.

(2)For a partnership or sole proprietorship: by general 				partner or the proprietor, respectively.

(3)For a municipality, State, Federal or other public 				agency: by either a principal executive officer or 				ranking elected official.  For purposes of this section, 			a principal executive officer of a Federal agency 					includes: (i) The chief executive officer of the agency, 			or (ii) a senior executive officer having responsibility 			for the overall operations of a principal geographic 				unit of the agency (e.g., Regional Administrators of 				EPA).

b.	All other reports required by this Order and other 				information requested by the Executive Officer shall be 			signed by a person described in paragraph a. of this 				reporting requirement, or by a duly authorized 						representative of that person.  A person is a duly 				authorized representative only if:

(1)The authorization is made in writing by a person 					described in paragraph a. of this reporting requirement;

(2)The authorization specifies either an individual or a 			position having responsibility for the overall operation 			of the regulated facility or activity, such as the 				position of plant manager, operator of a well or a well 			field, superintendent, or position of equivalent 					responsibility or an individual or position having 				overall responsibility for environmental matters for the 			company.  (A duly authorized representative may thus be 			either a named individual or any individual occupying a 			named position); and,

(3)The written authorization is submitted to the Executive 			Officer.

c.	If an authorization under paragraph b. of this reporting 		requirement is no longer accurate because a different 			individual or position has responsibility for the overall 		operation of the facility, a new authorization satisfying 		the requirements of paragraph b. of this section must be 		submitted to the Executive Officer prior to or together 			with any reports, information, or applications to be signed 		by an authorized representative.

d.	Any person signing a document under paragraph a. or b. of 		this section shall make the following certification:

"I certify under penalty of law that this document and all 		attachments were prepared under my direction or supervision 		in accordance with a system designed to assure that 				qualified personnel properly gather and evaluate the 				information submitted.  Based on my inquiry of the person 		or persons who manage the system, or those persons directly 		responsible for gathering the information, the information 		submitted is, to the best of my knowledge and belief, true, 		accurate, and complete.  I am aware that there are 				significant penalties for submitting false information, 			including the possibility of fine and imprisonment for 			knowing violations."

11.Except for data determined to be confidential under Title 40, 	United States Code of Federal Regulations Part 2, all reports 	prepared in accordance with the terms of this order shall be 	available for public inspection at the office of the Regional 	Board.  As required by the Clean Water Act, Reports of Waste 	Discharge, this Order, and effluent data shall not be 	considered confidential.

12.The Discharger shall comply with Monitoring and Reporting 	Program No. 99-47.

13.The Discharger shall submit reports and provide notifications 	as required by this order in accordance with the following:

(a)Reports required to be submitted to the Regional Board 			Executive Officer shall be sent to:

California Regional Water Quality Control Board

San Diego Region

9771 Clairemont Mesa Blvd, Suite A

San Diego, California 92124-1324

Notifications required to be provided to the Regional Board 		Executive Officer shall be made to:

Phone - (858) 467-2952

Fax -	(858) 571-6972

(b)Reports required to be submitted to the U.S. Environmental 		Protection Agency shall be sent to:

U.S. Environmental Protection Agency

Region IX

Permits Issuance Section

75 Hawthorne Street (W-5-1)

San Franciso, California 94105

(c)Notifications required to be provided to the California 			Department of Fish and Game shall be made to:

California Department of Fish and Game

4949 View Ridge Ave.

San Diego, CA 92123

San Diego Office

Phone - (858) 467-4218

Fax - (858) 467-4299

G. NOTIFICATIONS

1.	California Water Code Section 13263(g) states:

"No discharge of waste into waters of the state, whether or 	not such discharge is made pursuant to waste discharge 	requirements, shall create a vested right to continue such 	discharge.  All discharges of waste into waters of the state 	are privileges, not rights."

2.	The Clean Water Act provides that any person who violates 	section 301, 302, 306, 307, 308, 318 or 405 of the Act, or any 	permit condition or limitation implementing any such sections 	in a permit issued under section 402, or any requirement 	imposed in a pretreatment program approved under sections 	402(a)(3) or 402(b)(8) of the Act, is subject to a civil 	penalty not to exceed $25,000 per day for each violation.  The 	Clean Water Act provides that any person who negligently 	violates section 301, 302, 306, 307, 308, 318, or 405 of the 	Act, or any conditions or limitations implementing any of such 	sections in a permit issued under section 402 of the Act, or 	any requirement imposed in a pretreatment program approved 	under section 402(a)(3) or 402(b)(8) of the Act, is subject to 	criminal penalties of $2,500, to $25,000 per day of violation, 	or imprisonment of not more than 1 year, or both.  In the case 	of a second or subsequent conviction for a negligent 	violation, a person shall be subject to criminal penalties of 	not more than $50,000 per day of violation, or by imprisonment 	of not more than 2 years or both.  Any person who knowingly 	violates such sections, or such conditions or limitations is 	subject to criminal penalties of $5,000 to $50,000 per day of 	violation, or imprisonment for not more than 3 years, or both.  	In the case of a second or subsequent conviction for a knowing 	violation, a person shall be subject to criminal penalties of 	not more than $100,000 per day of violation, or imprisonment 	of not more than 6 years, or both.  Any person who knowingly 	violates section 301, 302, 306, 307, 308, 318 or 405 of the 	act, or any permit condition or limitation implementing any of 	such sections in a permit issued under section 402 of the Act, 	and who knows at that time that he thereby places another 	person in imminent danger of death or serious bodily injury, 	shall, upon conviction, be subject to a fine of not more than 	$250,000 or imprisonment of not more than 15 years, or both.  	In the case of a second or subsequent conviction for a knowing 	endangerment violation, a person shall be subject to a fine of 	not more than $500,000 or by imprisonment of not more than 30 	years, or both.  An organization, as defined in section 	309(c)(3)(B)(iii) of the CWA, shall, upon conviction of 	violating the imminent danger provision, be subject to a fine 	of not more than $1,000,000 and can be fined up to $2,000,000 	for second and subsequent violations.

3.	Any person may be assessed an administrative penalty by the 	Administrator for violating section 301, 302, 306, 307, 308, 	318, or 405 of this Act, or any permit condition or limitation 	implementing any of such sections in a permit issued under 	section 402 of this Act.  Administrative penalties for Class I 	violations are not to exceed $10,000 per violation, with the 	maximum amount of any Class I penalty assessed not to exceed 	$25,000.  Penalties for Class II violations are not to exceed 	$10,000 per day for each day during which the violation 	continues, with the maximum amount of any Class II penalty not 	to exceed $125,000.

4.	The Clean Water Act provides that any person who falsifies, 	tampers with, or knowingly renders inaccurate any monitoring 	device or method required to be maintained under this permit 	shall, upon conviction, be punished by a fine of not more than 	$10,000, or by imprisonment for not more than 2 years, or 	both.  If a conviction of a person is for a violation 	committed after a first conviction of such person under this 	paragraph, punishment is a fine of not more than $20,000 per 	day of violation, or by imprisonment of not more than 4 years, 	or both.

5.	Nothing in this Order shall be construed to preclude the 	institution of any legal action or relieve the Discharger from 	any responsibilities, liabilities, or penalties to which the 	Discharger is or may be subject to under Section 311 of the 	Clean Water Act.

6.	Nothing in this Order shall be construed to preclude the 	institution of any legal action or relieve the Discharger from 	any responsibilities, liabilities, or penalties established 	pursuant to any applicable State law or regulation under 	authority preserved by Section 510 of the Clean Water Act.

7.	This Order shall become effective 10 days after the date of 	its adoption provided the Regional Administrator, USEPA, has 	no objection.  If the Regional Administrator objects to its 	issuance, this Order shall not become effective until such 	objection is withdrawn.

8.	This Order supersedes Order No. 95-49.

9.	This Order shall serve as a National Pollutant Discharge 	Elimination System Permit pursuant to Section 402 of the Clean 	Water Act or amendments thereto.

Appendix A: Endnote References

Endnote References for Order No. 99-47 (NPDES No. CA0108073), WASTE DISCHARGE REQUIREMENTS FOR SOUTHERN CALIFORNIA EDISON COMPANY, SAN ONOFRE NUCLEAR GENERATING STATION, UNIT 2, SAN DIEGO COUNTY

1.	The effluent concentration limits for Ocean Plan Table B 	parameters were determined using the procedures outlined in 	the Ocean Plan and a minimum initial dilution value of ten.  	Background concentrations (Cs) were taken from influent data 	reported in the 1989 NPDES renewal application and from Table 	C of the Ocean plan.

2.	The mass emission rate (MER) of a substance is calculated 	using the following equation:

MER = 8.34 x Q x C

Where MER is the mass emission rate in lb/day, Q is the maximum discharge flowrate in MGD, and C is the effluent concentration in mg/l.  For flows where the discharge rate is below the maximum value, the actual value shall be used for calculation purposes, thus generating a MER value that is correspondingly lower.

If a composite sample is taken, C is the concentration 	measured in the composite sample and Q is the average 	discharge flowrate occurring during the period over which the 	composite sample is collected.

3.	The MER limits in this table were obtained using Q = 1286.9 	MGD (the maximum daily combined discharge flowrate reported in 	the Report of Waste Discharge) and effluent concentration 	limits determined as specified in Endnote 1.  When the 	combined discharge flowrate is lower than 1286.9 MGD, the MER 	limits shall be correspondingly lower.

4.	The six-month median effluent concentration limit shall apply 	as a moving median of daily values for any 180-day period in 	which daily values represent flow weighted average 	concentrations within a 24-hour period.  For intermittent 	discharges, the daily value shall be considered to equal zero 	for days on which no discharge occurred.

5.	The daily maximum effluent concentration limit shall apply to 	flow weighted 24-hour composite samples.

6.	The instantaneous maximum effluent concentration limit shall 	apply to grab sample determinations.

7.	The Discharger may at its option meet this limitation as a 	total chromium limitation.

8.	In samples obtained from marine, saline, or other waters 	containing bromine, total chlorine residual limitations shall 	apply to total residual oxidants.

Discharge Specification B.1

In Discharge Specification B.1, the total chlorine residual 	effluent limitations shown are for non-intermittent 	chlorine/bromine sources.  The 6-month median and daily 	maximum effluent limitations are based on the Ocean Plan water 	quality objectives using the procedure described in Endnote 1.  	The instantaneous maximum effluent limitation is based on the 	USEPA BAT effluent limitation contained in 40 CFR 423.  MER 	limits are calculated using maximum flowrates and the 	procedures described in Endnote 2.  When the flowrate is less 	than the maximum flowrate, the MER limit shall be 	correspondingly lower.

If the discharge of chlorine/bromine is an intermittent 	discharge not exceeding two hours, the total chlorine residual 	effluent limitation shall be the lower of the following:

(a)An effluent limitation calculated using the procedures 			described in Endnote 1 and water quality objectives 				determined through the use of the following equation:

log y = -0.43(log x) + 1.8 (Equation 3)

where:	y = the water quality objective (in ug/l) to apply 					when chlorine/bromine is being discharged;

x = the duration of uninterrupted chlorine/bromine 					discharge in minutes; or,

(b)the USEPA BAT effluent limitation contained in 40 CFR 423 		(0.20 mg/l).

MER limits for intermittent discharges shall be calculated 	using the following equation:

MER limit (lb/day) = 8.34 x C x Q x z/24

where:	C = effluent concentration limit as calculated above 				(mg/l)

Q = discharge flowrate (MGD)

z = total time (hours) chlorine/bromine is discharged 				per day, not to exceed two (2.0) hours per unit; or,

Discharge Specification B.16

In Discharge Specification B.16, effluent limitations for 	total chlorine residual are based on the Ocean Plan water 	quality objectives for non-intermittent chlorine/bromine 	sources using the procedure described in Endnote 1.  MER 	limits are calculated using maximum flowrates and the 	procedures described in Endnote 2.  When the flowrate is less 	than the maximum flowrate, the MER limit shall be 	correspondingly lower.

Effluent limitations for total chlorine residual applying to 	intermittent discharges not exceeding two hours shall be 	calculated using the procedure described in Endnote 1 and 	water quality objectives determined using Equation 3 and 	above.  MER limits shall be calculated using the following 	equation:

MER limit (lb/day) = 8.34 x C x Q x z/24

where:	C = effluent concentration limit as calculated 						above (mg/l)

Q = discharge flowrate (MGD)

z = total time (hours of chlorine/bromine is 						discharged per day, not to exceed two (2.0) hours 					per unit; or,

Receiving Water Limitation D.3

In Receiving Water Limitation D.3, limitations for total 		chlorine residual are for non-intermittent chlorine/bromine 	sources.  Water quality objectives for total chlorine residual 	applying to intermittent discharges not exceeding two hours 	shall be determined using Equation 3 above.

Total chlorine residual may be measured by either of the two 	EPA-approved analytical methods: amperometric titration or 	DPD-colorimetric.

9.	See Appendix I of the Ocean Plan for a definition of terms.

10.The monthly average is the arithmetic mean using the results 	of analyses of all samples collected during any 30-day 	consecutive calendar day period.

11.The weekly average is the arithmetic mean using the results 	of analyses of all samples collected during any 7 consecutive 	calendar day period.

12.Toxicity units are defined as follows.

Acute Toxicity

a.	Acute Toxicity (TUa)

Expressed in Toxic Units Acute (TUa)

TUa = 	 100

96-hr LC 50%

b.	Lethal Concentration 50% (LC 50)

LC 50 (percent waste giving 50% survival of test organisms) 		shall be determined by static or continuous flow bioassay 		techniques using standard test species.  If specific 				identifiable substances in wastewater can be demonstrated 		by the Discharger as being rapidly rendered harmless upon 		discharge to the marine environment, but not as a result of 		dilution, the LC 50 may be determined after the test 				samples are adjusted to remove the influence of those 			substances.

When it is not possible to measure the 96-hour LC 50 due to 		greater than 50 percent survival of the test species in 100 		percent waste, the toxicity concentration shall be 				calculated by the expression:

Chronic Toxicity

a. Chronic Toxicity (TUc)

Expressed as Toxic Units Chronic (TUc)

TUc = 	100

NOEL

b. No Observed Effect level (NOEL)

The NOEL is expressed as the maximum percent effluent or 		receiving water that causes no observable effect on a test 		organism, as determined by the result of a critical life 		stage toxicity test listed in Appendix II of the Ocean 			Plan.

13.The MER limits in this table were obtained using the 	indicated maximum flowrate and the following effluent 	concentration limits from the USEPA standards for the steam 	electric power generating point source category contained in 	40 CFR Part 423:

| Parameter | Units | Monthly Average | Daily Maximum | Instantaneous Maximum |
| --- | --- | --- | --- | --- |
| Total Suspended Solids | mg/l | 30.0 | 100.0 | 100.0 |
| Grease and Oil | mg/l | 15.0 | 20.0 | 20.0 |

When the discharge flowrate is lower than the maximum 	flowrate, the MER limit shall be correspondingly lower.

14.The MER limits in this table were obtained using the indicated 	maximum flowrate and effluent concentration limits from Table 	A of the Ocean Plan.  When the flowrate is lower than the 	indicated maximum flowrate, the MER limits shall be 	correspondingly lower.

I, John H. Robertus, Executive Officer, do hereby certify the foregoing is a full, true, and correct copy of an Order adopted by the California Regional Water Quality Control Board, San Diego Region, on August 11, 1999.

_____________________________

John H. Robertus

Executive Officer