CALIFORNIA REGIONAL WATER QUALITY CONTROL BOARD

SAN DIEGO REGION

ORDER NO. 2000-13

NPDES NO. 0107417

# WASTE DISCHARGE REQUIREMENTS

FOR THE

SOUTH EAST REGIONAL RECLAMATION AUTHORITY

ORANGE COUNTY

DISCHARGE TO THE PACIFIC OCEAN

THROUGH THE SOUTH EAST REGIONAL RECLAMATION AUTHORITY OCEAN OUTFALL

CALIFORNIA REGIONAL WATER QUALITY CONTROL BOARD

SAN DIEGO REGION

## Table of Contents

Findings	  2

- Prohibitions	 14

- Discharge Specifications	 15

- Receiving Water Limitations	 30

- Pretreatment Requirements	 37

- Sludge Requirements	 40

- Provisions	 43

- Reporting Requirements	 54

- Notifications	 63

- Order No. 2000-13 Endnotes	 64

- Attachment 1 (Ocean Plan Discharge Prohibitions) 	 66

- Attachment 2 (Basin Plan Discharge Specifications) 	 67

- Attachment 3 (Standard Provisions from 40 CFR 122.41-42) 	 69

- Attachment 4 (Standard Provisions 40 CFR by Reference) 	 73

- Attachment 5 (Map of SERRA Ocean Outfall and Service Area)	117

- Attachment 6 (Regional Board Contact Information)	118

Monitoring and Reporting Program No. 2000-13	119

- Purpose	119

- Monitoring Provisions	119

- Influent Monitoring	122

- Effluent Monitoring	123

- Solids Monitoring	126

- Receiving Water Monitoring	126

- Monitoring and Reporting Program Endnotes	134

The California Regional Water Quality Control Board, San Diego Region (hereinafter Regional Board), finds that:

- On February 10, 1995, this Regional Board adopted Order No. 95-01, National Pollution Discharge Elimination System (NPDES) No. CA0107417, Waste Discharge Requirements for the South East Regional Reclamation Authority Ocean Outfall, Orange County, which superseded Order No. 88-71.  Order No. 95-01 maintained the requirement for the discharge of an average dry weather flow-rate of 30.0 million gallons per day (MGallons/Day) of secondary-treated wastewater to the Pacific Ocean via the South East Regional Reclamation Authority (SERRA) Ocean Outfall, as was established in Order No. 88-71.  Order No. 95-01 contained an expiration date of February 9, 2000.

- On June 8, 1995, this Regional Board adopted Technical Change Order No. 1 to Monitoring and Reporting Program No. 95-01 for the South East Regional Reclamation Authority Ocean Outfall.  This technical change order supersedes Monitoring and Reporting Program No. 95-01 in its entirety, and became effective on July 1, 1995.

- On September 23, 1999, SERRA submitted an application for renewal of its NPDES permit pursuant to Reporting Requirement No. E.1. of Order No. 95-01.  This Order is a renewal of the NPDES permit and supersedes Order No. 95-01.

- The South East Regional Reclamation Authority (SERRA) is a joint powers authority formed to operate regional sewage treatment and disposal facilities, including an ocean outfall, for the benefit of its member agencies.  SERRA encompasses that area of south Orange County north of the Orange/San Diego County boundary and south of the Aliso Water Management Agency (AWMA) jurisdiction.  SERRA consists of the following five member agencies:  the South Coast Water District (SCWD), the Moulton-Niguel Water District (MNWD), the Santa Margarita Water District (SMWD), the City of San Clemente (CSC) and the City of San Juan Capistrano (CSJC).  Wastewater generated in the SERRA service area is treated at one of five treatment facilities in the SERRA Agency system identified in Finding No.6 of this order.  Attachment No.5 of this Order shows the location of the treatment facilities tributary to the SERRA Ocean Outfall.

- On January 7, 1999, the South Coast Water District consolidated the Dana Point Sanitary District (DPSD) and the Capistrano Beach Water District (CBWD) into its service area.  Wastewater from a portion of the South Coast Water District service area is treated at the Jay B. Latham Regional Treatment Plant, after which it is discharged to the ocean through the SERRA Ocean Outfall.

- The following table identifies the treatment facilities that discharge to the SERRA Ocean Outfall, their current and projected capacities, and discharge rates.

| Treatment Facility | Existing Secondary Treatment Design Capacity (Mgallons/Day*) | 1998 Discharge Rate to SERRA Ocean Outfall (Mgallons/Day *) | Planned 2005 Secondary Treatment Design Capacity (Mgallons/Day *) | Projected 2005 Discharge Rate to SERRA Ocean Outfall (Mgallons/Day *) |
| --- | --- | --- | --- | --- |
| SERRA Jay B. Latham Regional Treatment Plant | 13.0 | 9.2 | 13.0 | 13.0 |
| City of San Clemente WRF | 6.98 | 4.4 | 6.98 | 6.0 |
| SMWD Chiquita WRP | 6.0 | 3.5 | 9.0 | 5.0 |
| MNWD 3a Reclamation Plant | 6.0 | 2.0 | 6.0 | 6.0 |
| SMWD Oso Creek WRP | 3.0 | 0.0 | 3.0 | 0 |
| TOTAL | 34.98 | 19.1 | 37.98 | 30.0 |

*Average dry-weather flowrate.

The MNWD 3A and SMWD Oso Creek Water Reclamation Plants were intended to treat the volume of wastewater needed for reclamation purposes. The wastewater collection and conveyance system is designed such that any wastewater not treated at these plants is conveyed to the SERRA Jay B. Latham Regional Treatment Plant for treatment and disposal to the ocean through the SERRA Ocean Outfall.  Currently, the MNWD 3A Plant treats all MNWD wastewater flows that are tributary to the plant.  The wastewater from the SMWD Oso Creek Water Reclamation Plant service area that is not reclaimed is sent to the SERRA Jay B. Latham Regional Treatment Plant for service.  Wastewater treated at the MNWD 3A plant, but not reused, can be discharged directly to the ocean through the SERRA Ocean Outfall via the San Juan Basin Authority Bypass without additional treatment at the SERRA Jay B. Latham Regional Treatment Plant.

- The SERRA Jay B. Latham Regional Treatment Plant, located at 34156 Del Obispo, Dana Point, adjacent to San Juan Creek, is a conventional activated sludge treatment facility.  Wastewater treatment unit operations and processes are screening, grit removal, primary clarification and secondary treatment using an activated sludge process consisting of aeration and clarification. The plant’s design capacity is 13 Mgallons/Day.  The plant has chlorination facilities, but only uses the facilities to manage microbiological growth  Waste sludge is thickened, digested, dewatered and transported to a privately owned and operated composting facility, a permitted land application sites or permitted sanitary landfill. All effluent from the SERRA Jay B. Latham Regional Treatment Plant is discharged to the Pacific Ocean through the SERRA Ocean Outfall.

- The SMWD Oso Creek Water Reclamation Plant, located at 27204 East La Paz Road, Mission Viejo, adjacent to Oso Creek, is an activated sludge treatment facility with a capacity to treat 3 Mgallons/Day.  Wastewater treatment unit operations and processes at the SMWD Oso Creek Reclamation Plant are microscreening, aeration, clarification, filtration and chlorine disinfection.  Only effluent intended to be used for irrigation is chlorinated.  Waste solids and filter backwash are transported to the SERRA Jay B. Latham Regional Treatment Plant via the Oso-Trabuco Interceptor Sewer.  Secondary effluent is directed to an onsite advanced water reclamation facility for further treatment and pumped to the Upper Oso Reservoir.  There is no connection from the Oso Creek Reclamation Plant to the SERRA Ocean Outfall.  In situations when the plant is off-line, the raw wastewater flows to the SERRA Jay B. Latham Regional Treatment Plant, where it is treated and then discharged through the SERRA Ocean Outfall.

- The MNWD 3A Reclamation Plant, located at 26801 Camino Capistrano, Mission Viejo, adjacent to Oso Creek, is a conventional activated sludge treatment facility.  In 1991, MNWD submitted a report for the Water Reclamation Expansion Project.  The design capacity for secondary treatment increased from 2.5 Mgallons/Day to 6.0 Mgallons/Day.  Wastewater treatment unit operations and processes at the MNWD 3A Reclamation Plant are screening, aerated grit removal, primary sedimentation, aeration, clarification, filtration and chlorine disinfection. Only effluent intended to be used for irrigation is chlorinated. Waste activated sludge is thickened by air flotation, stabilized by anaerobic digestion, and dewatered.  The dewatered sludge is hauled to a sanitary landfill or to a privately owned and operated composting facility. Secondary effluent is either directed to an on-site advanced water reclamation facility for further treatment or is discharged through the SERRA Ocean Outfall via the San Juan Basin Authority Bypass, and the Chiquita Land Outfall.

- The SMWD Chiquita Reclamation Plant, located at 28793 Ortega Highway, San Juan Capistrano, is a high-rate trickling filter treatment facility.  Wastewater treatment unit operations and processes are screening, grit removal, primary clarification and secondary treatment using a combination of high-rate trickling filtration, recirculation, solids contact, and secondary clarification.  The plant has chlorination facilities which are not being used at this time.  Primary and secondary sludges are mixed, thickened, digested, dewatered and transported either to a privately owned and operated composting facility in Riverside County or to a sanitary landfill for disposal.  SMWD is proposing to expand the current design of 6.0 Mgallons/Day to 9.0 Mgallons/Day by 2001.  The SMWD is also proposing to construct advanced wastewater treatment facilities at the Chiquita Reclamation Plant in the future to provide recycled water for irrigation.  Currently all effluent from the SMWD Chiquita Reclamation Plant is discharged through the SERRA Ocean Outfall via the Chiquita Land Outfall.

- The City of San Clemente Reclamation Plant, located at 380 Avenida Pico, San Clemente, is a conventional activated sludge treatment facility, with a capacity of 6.98 Mgallons/Day.  Wastewater treatment and unit operations and processes are screening, grit removal, primary clarification and secondary treatment using an activated sludge process consisting of aeration and clarification.  The plant has chlorination facilities, but only effluent intended to be used for irrigation is chlorinated.  Settled primary sludges and skimmings are pumped to a two-stage anaerobic digestion process.  Waste sludge is thickened, digested, dewatered and transported to a privately owned and operated composting facility.  A small portion of dewatered sludge is sent to a sanitary landfill for disposal.  Secondary effluent is either directed to an on-site advanced water reclamation facility for further treatment or discharged through the SERRA Ocean Outfall via the San Clemente Land Outfall.

- The San Clemente Land Outfall routes treated wastewater from the City of San Clemente Reclamation Plant northwesterly to the junction with the SERRA Ocean Outfall.  This land outfall is approximately 4.4 miles long with a capacity of 14 Mgallons/Day.  Effluent from the City of San Clemente Reclamation Plant that is not reused enters this land outfall and is discharged to the Pacific Ocean through the SERRA Ocean Outfall (shown on Attachment No. 5).

- The Chiquita Land Outfall extends from the SMWD Chiquita Water Reclamation Plant southwesterly past the junction with the San Juan Basin Authority Bypass, to the junction with the SERRA Ocean Outfall.  This land outfall is 6 miles long with a capacity of 42 Mgallons/Day.  All effluent from the Chiquita Reclamation Plant enters this land outfall and is discharged to the Pacific Ocean via the SERRA Ocean Outfall (shown on Attachment No. 5).

- The San Juan Basin Authority Bypass pipeline begins at the SMWD Oso Creek Barrier past the MNWD 3A Reclamation Plant, and continues in a southerly direction to the junction with the Chiquita Land Outfall.  This land outfall is 5.9 miles long with a capacity of 6 Mgallons/Day.  Effluent from the MNWD 3A Reclamation Plant is discharged to the Pacific Ocean via the SERRA Ocean Outfall (shown on Attachment No. 5).

- This Regional Board regulates the reuse of recycled wastewater from SERRA-member agency plants, by various orders that serve as State Waste Discharge Requirements.

a.	This Regional Board’s Order No. 97-52 , Waste Discharge and Water Recycling Requirements for the Production and Purveyance of Recycled Water by Member Agencies of the South Orange County Reclamation Authority, Orange County, prescribes recycled water production and purveyance requirements to the South Orange County Reclamation Authority (SOCRA) and its member agencies, listed in the table below:

SOCRA MEMBER AGENCIES

| AGENCIES | MEMBERSHIP STATUS |
| --- | --- |
| Capistrano Valley Water District El Toro Water District Irvine Ranch Water District Los Alisos Water District Moulton Niguel Water District Santa Margarita Water District South Coast Water District Trabuco Canyon Water District | MEMBER MEMBER MEMBER MEMBER MEMBER MEMBER MEMBER MEMBER |

Reclaimed wastewater discharges from the MNWD 3A Reclamation Plant, the SMWD Chiquita Reclamation Plant and the SMWD Oso Creek Reclamation Plant are regulated under Order No. 97-52. South Coast Water District has an agreement with Moulton Niguel Water District to provide up to 1000 acre-feet per year to Moulton Niguel Water District for distribution.

b.	The City of San Clemente is not a member of SOCRA, however, the City of San Clemente may provide recycled water to SOCRA for distribution within the SOCRA service area.  The City of San Clemente's Water Reclamation Plant is regulated under Order No. 91-50, Waste Discharge Requirements for the City of San Clemente Water Reclamation Plant, Reclamation Projects, Orange County.

- The current SERRA Ocean Outfall has been in use since 1978.  The outfall extends approximately 10,550 feet offshore in a southwesterly direction from Doheny State Beach.  The inshore end of the diffuser is located approximately 10,334 feet offshore at a depth of approximately 100 feet.  The first portion of the diffuser (216) feet is collinear with the rest of the outfall.  The remaining portion of the diffuser, at a depth of approximately 100 feet, extends 1272 feet in a northwesterly direction, perpendicular to the rest of the outfall, and terminates at Latitude 33 26’ 10” N, Longitude 117 41’ 53” W.  Effluent pumping to the ocean outfall is required when peak flow conditions coincide with extreme high tide conditions.  The design capacity of the SERRA Ocean Outfall is 24 Mgallons/Day for gravity flow.  The design capacity of the SERRA Ocean Outfall pumping facilities is 107 Mgallons/Day.  Attachment No. 5 shows the location of the SERRA Ocean Outfall.

- SERRA has proposed the construction of two groundwater desalting plants which would discharge brine through the SERRA Ocean Outfall.

a.	One of the proposed groundwater desalting plants would be constructed by the South Coast Water District, on a two-acre site adjacent to the San Juan Creek, approximately one-half mile north of the Pacific Coast Highway.  The plant will treat groundwater by  reverse osmosis (RO) with ion exchange presoftening. Sodium chloride will be added to the brine produced during RO treatment, and this mixture will be used to regenerate the ion exchange softeners.  A waste stream from this regeneration process of 0.32 Mgallons/Day will be discharged through the Chiquita Land Outfall to the SERRA Ocean Outfall.

b.	The other proposed desalting plant, adjacent to San Juan Creek, immediately north of the I-5 Freeway, will be owned and operated by the San Juan Basin Authority (SJBA).  This project will be constructed in phases. Phase 1 will have a production capacity of 4.02 Mgallons/Day.  Subsequent phases will be sized and developed based on operation and groundwater management experience gained during the Phase 1 operation.  The treatment process will consist of pretreatment for the removal of iron, manganese and hardness, followed by RO, aeration, pH adjustment and disinfection. The projected quantity of the brine discharge from this treatment plant is 0.73 million gallons per day.

- SERRA and their consultant, Boyle Engineering Corporation, determined the minimum initial dilution for the SERRA Ocean Outfall, using the computer model UMERGE, to be 109. The values they calculated are slightly lower than the initial dilution of 116 cited in Order No 95-01.  The initial dilution of 116 was derived by the staff of the State Water Resources Control Board using the UPLUME computer model.  This newly derived indilution factor is based on 30 Mgallons/Day of secondary effluent.  The addition of 1.05 Mgallons/Day of brine wastes to the secondarily treated wastewater would reduce the minimum indilution dilution to 100.  This permit will use the initial dilution factors determined by SERRA until the reevaluation of the initial dilution factors by the State Board is complete. At that point, the initial dilution may be changed. As it is not certain at this time whether either of the proposed groundwater desalination plants will be constructed, this permit contains two sets of effluent discharge limits.  In the case of no brine discharge, the effluent limitations will be based on an initial dilution value of 109.  The effluent limitations for secondary effluent combined with brine will be based on an initial dilution of 100.

- In the permit renewal application, SERRA has reported on several seasonal nuisance water diversion discharges to the sewage collection systems within the SERRA Agency system.  These nuisance flow projects would keep dry-weather low-volume stormwater flows in specific storm drains from crossing the beaches to the ocean by diverting the nuisance flows to the sewer systems.  The purpose of these diversions is to mitigate the possible threat to public health caused by high bacteria levels and other contaminants associated with urban runoff.  The current and proposed storm drain diversions are described below.

a.	Two South Coast Water District diversion projects are currently in operation.  The first project is located just north of “Baby Beach” in Dana Point Harbor, where twice weekly, approximately 5,000 gallons of nuisance water basis is pumped from the storm drain to the headworks of the SERRA plant, where it is treated with the sewage influent to the plant.  The second project diverts nuisance water from a natural drainage culvert located between the Doheny State Park and a Dana Point Harbor parking lot.  The nuisance water, of an estimated average flow of 10,000 gallons/day, is transported to the headworks of the SERRA plant, where it is treated with the sewage influent to the plant.

b.	The South Coast Water District has proposed a nuisance water diversion along Camino Capistrano at Camino de Estrella.  This project would divert flow of approximately 1,000 gallons per day to the SERRA treatment plant. The City has also proposed a nuisance water diversion project from twenty-six storm drain pipes along Pacific Coast Highway in the Capistrano Beach area.  This project would divert as much as approximately 10,000 gallons per day of nuisance flow to the SERRA treatment plant.  Both projects are scheduled for Spring 2000.

c.	The City of San Clemente has applied to divert seasonal nuisance water from two storm drain locations to the wastewater collection system.  The storm drains are located at Riviera Beach and Linda Lane. An estimate of flow is not yet available.  Construction of the system is planned for Spring 2000.  The City of San Clemente is considering other low-flow nuisance water diversion projects within the next two years.  Possible projects include a system for capturing and diverting the first-flush stormwater, and diversion of nuisance water to the sewer treatment plant from the coastal area in the proposed 250-acre Marblehead Coastal project.  Another possible project is the diversion of low-flow nuisance water from Segunda Deschecha Canada channel to the wastewater treatment plant or to the land outfall for direct discharge into the ocean.

20.	The SWRCB adopted a revised Water Quality Control Plan for Ocean Waters of California (California Ocean Plan) on July 23, 1997.  The Ocean Plan identifies the following beneficial uses of state ocean waters to be protected:

- Industrial water supply

b.	Navigation

c.	Water contact recreation

d.	Non-contact water recreation

e.	Ocean commercial and sport fishing

f.	Preservation and enhancement of Areas of Special Biological Significance

g.	Preservation of rare and endangered species

h.	Marine habitat

i.	Mariculture

j.	Fish migration

k.	Fish spawning

l.	Shellfish harvesting

m.	Aesthetic enjoyment

In order to protect these beneficial uses, the Ocean Plan establishes water quality objectives (for bacterial, physical, chemical, and biological characteristics, and for radioactivity), general requirements for management of waste discharge to the ocean, quality requirements for waste discharges (effluent water quality requirements), discharge prohibitions, and general provisions.

21.	The Comprehensive Water Quality Control Plan Report, San Diego Basin (9), (Basin Plan) was adopted by this Regional Board on March 17, 1975 and subsequently approved by the SWRCB. Subsequent revisions to the Basin Plan have also been adopted by the Regional Board and approved by the SWRCB.

22.	The Basin Plan identifies the following beneficial uses of state ocean waters to be protected:

- Industrial service supply

- Navigation

- Water contact recreation

- Noncontact water recreation

- Ocean commercial and sport fishing

- Preservation of Areas of Special Biological Significance (ASBS)

- Preservation of rare and endangered species

- Marine habitat

- Mariculture

- Fish migration

- Fish spawning

- Shellfish harvesting

- Wildlife habitat

The Basin Plan relies primarily on the requirements of the Ocean Plan for protection of these beneficial uses.  However, the Basin Plan establishes additional water quality objectives for dissolved oxygen and pH.

23.	The 1997 Ocean Plan states that, “Water shall not be discharged to areas designated as being of special biological significance.  Discharges shall be located a sufficient distance from such designated areas to assure maintenance of natural water quality conditions in that area.”

The marine habitat beneficial use identified in both the Ocean Plan and Basin Plan provides for the preservation of the marine ecosystems in the following Marine Life Refuges in the vicinity of the SERRA Ocean Outfall: the Laguna Beach Marine Life Refuge, the South Laguna Beach Marine Life Refuge, the Dana Point Marine Life Refuge, the Doheny Beach marine Life Refuge, and the Niguel Marine Life Refuge, all of Orange County.  The legal descriptions of the boundaries of these marine life refuges are contained in the Fish and Game Code of California, Division 7 (Refuges), Chapter 2(Refuges and Other Protected Areas), Article 6 (Marine Life Refuge).

Regional Board staff’s review of the monitoring data submitted by the discharger in accordance with the Monitoring and Reporting Program of Order No. 95-01 have not revealed any impacts on the above-listed Marine Life Refuges resulting from the SERRA Ocean Outfall discharge.  No impacts to the refuge areas are expected to occur in the future.

24.	State Board Resolution No. 74-28, Areas of Special Biological Significance, requires the Regional Boards to select areas in coastal waters which contain “biological communities of such extraordinary, even though unquantifiable, value that no acceptable risk of change in their environments as a result of man’s activities can be entertained.”  In the San Diego Region, Areas of Special Biological Significance (ASBS) include the Heisler Park Ecological Reserve, Orange County.  The location of the Preserve is defined in Chapter Five of the San Diego Basin Plan.

As stated in the Basin Plan, discharges of wastewaters and/or heat must be sufficiently removed spatially from these areas to assure the maintenance of natural water quality in the area.  Existing wastewater and/or heat discharges which influence the natural water quality in the designated area must be phased out as promptly as possible.

Regional Board staff’s review of the monitoring data submitted by the discharger in accordance with the Monitoring and Reporting Program of Order No. 95-01 have not revealed any impacts on the Heisler Park Ecological Reserve resulting from the SERRA Ocean Outfall discharge.  No impacts to this ASBS are expected to occur in the future.

25.	Receiving Water Limitation No. C.2a. of this Order establishes bacterial objectives for areas where shellfish may be harvested for human consumption, as determined by the Regional Board.  The Basin Plan establishes Dana Point Harbor as a shellfish harvesting area. Receiving Water Limitation No. C.2a, therefore, applies to the Dana Point Harbor.

26.	Federal regulations (40 CFR Part 403) establish pretreatment program requirements for POTWs which receive pollutants from industries subject to pretreatment standards.  This order contains industrial pretreatment program requirements pursuant to 40 CFR Part 403.

27.	On February 9, 1983, United States Environmental Protection Agency (USEPA), Region 9 granted final Industrial Pretreatment Program approval to SERRA. SERRA carries out pretreatment program activities for the following SERRA member agencies: City of San Clemente, SCWD, SMWD, City of San Juan Capistrano, and MNWD. Industrial permits are issued and their discharges are evaluated by SERRA.  SERRA is ultimately responsible for the pretreatment program in the area tributary to the SERRA Ocean Outfall.

28.	On November 16, 1990, the USEPA promulgated NPDES permit application requirements for stormwater discharges (40 CFR Parts 122, 123, and 124) which are applicable to wastewater treatment facilities tributary to the SERRA Ocean Outfall.  On April 17, 1997 the State Water Resources Control Board adopted Water Quality Order No. 97-03-DWQ, National Pollutant Discharge Elimination System (NPDES) General Permit No. CAS000001, Waste Discharge Requirements for Discharges of Storm Water Associated with Industrial Activities Excluding Construction Activities.  Storm water discharges from wastewater treatment facilities tributary to the SERRA Ocean Outfall are subject to the terms and conditions of Water Quality Order No. 97-03-DWQ, as amended.

29.	On February 19, 1993, the USEPA issued the final rule for the use and disposal of sewage sludge (40 CFR Part 503).  This regulation requires that producers of sewage sludge meet certain reporting, handling, and disposal requirements.  USEPA will oversee compliance with 40 CFR Part 503.

30.	Section 301(b)(1)(B) of the Clean Water Act (CWA) requires POTWs to meet effluent limitations based on secondary treatment as defined by the USEPA Administrator.  Secondary treatment is defined by the USEPA Administrator in the federal regulations (40 CFR Part 133.100 to 40 CFR Part 133.105) in terms of three parameters: 5-day biochemical oxygen demand (BOD5), total suspended solids (TSS), and pH.  Federal regulations allow substitution of 5-day carbonaceous biochemical oxygen demand (CBOD5) limitations for BOD5 limitations.  By letter dated April 16, 1990, SERRA requested that CBOD5 limitations be incorporated in the SERRA permit renewal in lieu of BOD5 requirements.  Following the approval of this Regional Board, Order No. 94-105 was modified to establish limits for CBOD5 , replacing BOD5 limitations.  This permit continues to reflect that change.  Discharge Specification B.1.a. of this Order establishes effluent limitations for CBOD5, TSS, and pH in accordance with federal secondary treatment regulations.  In addition, Discharge Specification B.1.a of this Order establishes  "Maximum at Any Time" limitations for CBOD5 and TSS based on best professional judgement.  Mass emission rate (MER) limitations have been calculated using a flow rate of 30 Mgallons/Day.

31.	Effluent limitations, industrial pretreatment standards, sludge use and disposal regulations, and ocean discharge criteria established under Sections 208(b), 301, 302, 303(d), 304, 306, 307, 403, and 405 of the CWA, as amended (Title 33 United States Code (USC) 1251 et seq.), are applicable to the discharge.

32.	On May 9, 1996, this Regional Board adopted Order No. 96-04, General Waste Discharge Requirements Prohibiting Sanitary Sewer Overflows by Sewage Collection Agencies, and addenda thereto, to regulate sewage discharges from publicly owned sewage collection systems in the San Diego Region.  Order No. 96-04, serving as State Waste Discharge Requirements, prohibits the discharge of sewage from sanitary sewer systems at any point upstream of a sewage treatment plant.  Order No. 96-04 requires the development of a Sanitary Sewer Overflow Prevention Plan and a Sanitary Sewer Overflow Response Plan for each collection system in the Region.  In the event that a sewage discharge occurs within a collection system, Order No. 96-04 specifies procedures for reporting the discharge to the Regional Board.

33.	Waste discharge requirements for this discharge must be in conformance with 40 CFR 131.12 and State Board Resolution No. 68-16, Statement of Policy with Respect to Maintaining High Quality of Waters in California (known collectively as "antidegradation" policies).   The Regional Board has taken into consideration the requirements of the State and Federal “antidegradation” policies in establishing the requirements contained herein, and has determined that any reduction in water quality as a result of this discharge will not result in any long-term deleterious effects on water quality.

34.	Monitoring and Reporting Program No. 2000-13 may be subject to changes during the 5 -year period of this permit.  The Southern California Coastal Water Research Project (SCCWRP) is currently investigating more effective techniques to monitor receiving waters of the Pacific Ocean.  Once the SCCWRP study is complete, these methods may be incorporated into this Order’s Monitoring and Reporting Program through an Addendum to this Order.

35.	The Regional Board, in establishing the requirements contained herein, considered factors including, but not limited to, the following:

a.	Beneficial uses to be protected and the water quality objectives

reasonably required for that purpose;

- Other waste discharges;

c.	The need to prevent nuisance;

d.	Past, present, and probable future beneficial uses of water;

e.	Environmental characteristics of the receiving waters under consideration,

including the quality of those receiving waters;

f.	Water quality conditions that could reasonably be achieved through the coordinated control of all factors that affect water quality in the area;

- Economic considerations;

h.	The need for developing housing within the region; and

i.	The need to develop and use recycled water.

36.	The issuance of waste discharge requirements for this discharge is exempt from the requirement for preparation of environmental documents under the California Environmental Quality Act (Public Resources Code, Division 13, Chapter 3, Section 21000 et seq.) in accordance with the California Water Code, Section 13389.

37.	The Regional Board has notified SERRA and all known interested parties of its intent to reissue the NPDES permit for the discharge through the SERRA Ocean Outfall to the Pacific Ocean.

38.	The Regional Board, in a public hearing on February 9, 2000, has heard and considered all comments pertaining to the discharge from the SERRA member-agency wastewater treatment facilities to the Pacific Ocean via the SERRA Ocean Outfall.

39.	This Order shall serve as a NPDES Permit for the discharge from the South East Regional Reclamation Authority Ocean Outfall to the Pacific Ocean pursuant to Section 402 of the Clean Water Act, and amendments thereto.

IT IS HEREBY ORDERED that the South East Regional Reclamation Authority (hereinafter discharger), in order to meet the provisions contained in Division 7 of the California Water Code and regulations adopted thereunder and the provisions of the Clean Water Act and the regulations adopted thereunder, shall comply with the following for the handling, treatment, and disposal of wastes through the South East Regional Reclamation Authority Ocean Outfall.

A.	PROHIBITIONS

1.	Discharges of wastes in a manner or to a location which have not been specifically authorized by this Order and for which valid waste discharge requirements are not in force are prohibited.

2.	The discharge of any radiological, chemical, or biological warfare agent, or high level radiological waste to the ocean is prohibited.

3.	The dumping or deposition, from shore or from vessels, of oil, garbage, trash or other solid municipal, industrial, or agricultural waste directly into waters subject to tidal action or adjacent to waters subject to tidal action in any manner which may permit it to be washed into waters subject to tidal action is prohibited.

4.	Waste shall not be discharged to areas designated as being of special biological significance.  Discharges shall be located a sufficient distance from such designated areas to assure maintenance of natural water quality conditions in these areas.

5.	Pipeline discharge of sludge to the ocean is prohibited by federal law; the discharge of municipal and industrial waste sludge directly to the ocean, or into a waste stream that discharges to the ocean, is prohibited.

6.	The discharge of sludge digester supernatant directly to the ocean, or into a waste stream that discharges to the ocean, without further treatment is prohibited.

7.	The bypassing of untreated wastes containing concentrations of pollutants in excess of those in Ocean Plan Table A or Table B or the effluent limitations of this Order to the ocean is prohibited, except as provided for in Provision F.36 of this Order.  (Also see Attachment No. 1 to this Order, 1997 Ocean Plan Discharge Prohibitions)

8.	Discharge through the SERRA Ocean Outfall from any treatment facility at a 30-day average dry weather flowrate in excess of the secondary treatment design capacity of that treatment facility is prohibited.  For the purposes of this Order, the secondary treatment design capacity of a treatment facility is the existing secondary treatment design capacity of that treatment facility identified in the findings of this Order unless the discharger obtains the Executive Officer's approval of a revised design capacity in accordance with Provision F.17.

9.	Compliance with Discharge Prohibitions as stated in Chapter V of the 1997 Ocean Plan (Attachment No. 1) is required as a condition of this Order.

10.	Compliance with the Waste Discharge Prohibitions contained in the 1994 Basin Plan (Attachment No. 2) is also required as a condition of this Order.

11.	Discharge to the Pacific Ocean from the treatment facilities in the SERRA agency system, including any discharge from the proposed desalinization plants, via the SERRA Ocean Outfall in excess of 30.0 MGallons/ Day average dry weather flow is prohibited unless the discharger obtains revised waste discharge requirements authorizing an increased flowrate.

B.	DISCHARGE SPECIFICATIONS

1.	The following effluent limitations, calculated using an initial dilution factor of 109, apply to the undiluted secondary effluent, with no brine waste, discharged from the SERRA member agency treatment plants via the SERRA Ocean Outfall.

a.	Effluent Limitations for Major Constituents and Properties of Wastewater

b.	Effluent Limitations on Toxic Materials for Protection of Marine Aquatic Life3

| Constituent | Units | 6-Month Median | Daily Maximum | Instantaneous Maximum |
| --- | --- | --- | --- | --- |
| Arsenic | ug/L | 553.00 | 3193.00 | 8473.00 |
|  | lb/Day | 138.36 | 798.89 | 2119.94 |
| Cadmium | ug/L | 110.00 | 440.00 | 1100.00 |
|  | lb/Day | 27.52 | 110.09 | 275.22 |
| Chromium (hexavalent)4 | ug/L | 220.00 | 880.00 | 2200.00 |
|  | lb/Day | 55.04 | 220.18 | 550.44 |
| Copper | ug/L | 112.00 | 1102.00 | 3082.00 |
|  | lb/Day | 28.02 | 275.72 | 771.12 |
| Lead | ug/L | 220.00 | 880.00 | 2200.00 |
|  | lb/Day | 55.04 | 220.18 | 550.44 |
| Mercury | ug/L | 4.35 | 17.55 | 43.95 |
|  | lb/Day | 1.09 | 4.39 | 11.00 |
| Nickel | ug/L | 550.00 | 2200.00 | 5500.00 |
|  | lb/Day | 137.61 | 550.44 | 1376.10 |
| Selenium | ug/L | 1650.00 | 6600.00 | 16500.00 |
|  | lb/Day | 412.83 | 1651.32 | 4128.30 |
| Silver | ug/L | 32.06 | 180.56 | 477.56 |
|  | lb/Day | 8.02 | 45.18 | 119.49 |
| Zinc | ug/L | 1328.00 | 7928.00 | 21128.00 |
|  | lb/Day | 332.27 | 1983.59 | 5286.23 |
| Cyanide5 | mg/L | 0.11 | 0.44 | 1.10 |
|  | lb/Day | 27.52 | 110.09 | 275.22 |
| Total Chlorine Residual6 | mg/L | 220.00 | 880.00 | 6600.00 |
|  | lb/Day | 55044.00 | 220176.00 | 1651320.00 |
| Ammonia (as N) | mg/L | 66000.00 | 264000.00 | 660000.00 |
|  | lb/Day | 16513200.00 | 66052800.00 | 165132000.00 |
| Chronic Toxicity | TUc |  | 110 |  |
| Phenolic Compounds | mg/L | 3.30 | 13.20 | 33.00 |
|  | lb/Day | 8.25.66 | 3302.64 | 8256.60 |
| Chlorinated phenolics | mg/L | 0.11 | 0.44 | 1.10 |
|  | lb/Day | 27.52 | 110.09 | 275.22 |

c.	Effluent Limitations for Toxic, Non-carcinogenic Materials for Protection of Human Health3

d.	Effluent Limitations for Toxic, Carcinogenic Materials for Protection of Human Health3

mg/L	=		milligrams per liter

ug/L		=		micrograms per liter

ng/L		=		nanograms per liter

pg/L		= 		picograms per liter

mL/L 	= 		milliliters per liter

NTU 	= 		Nephelometric Turbidity Units

TUa 		= 		toxic units acute

TUc 		= 		toxic units chronic

lb/Day 	= 		pounds per day

- The following effluent limitations, calculated using an initial dilution factor of 100, apply to the combined flow of secondary effluent and any brine wastes from either one or both of the groundwater desalting plants described in Finding No. 17 of this order, discharged from the SERRA member agency treatment plants via the SERRA Ocean Outfall.

- Effluent Limitations for Major Constituents and Properties of Wastewater

b.	Effluent Limitations on Toxic Materials for Protection of marine Aquatic Life3

| Constituent | Units | 6-Month Median | Daily Maximum | Instantaneous Maximum |
| --- | --- | --- | --- | --- |
| Arsenic | ug/L | 508.00 | 2932.00 | 7780.00 |
|  | lb/Day | 127.10 | 733.59 | 1946.56 |
| Cadmium | ug/L | 101.00 | 404.00 | 1010.00 |
|  | lb/Day | 25.27 | 101.08 | 252.70 |
| Chromium (hexavalent)4 | ug/L | 202.00 | 808.00 | 2020.00 |
|  | lb/Day | 50.54 | 202.16 | 505.40 |
| Copper | ug/L | 103.00 | 1012.00 | 2830.00 |
|  | lb/Day | 25.77 | 253.20 | 708.07 |
| Lead | ug/L | 202.00 | 808.00 | 2020.00 |
|  | lb/Day | 50.54 | 202.16 | 505.40 |
| Mercury | ug/L | 3.99 | 16.11 | 40.35 |
|  | lb/Day | 1.00 | 4.03 | 10.10 |
| Nickel | ug/L | 505.00 | 2020.00 | 5050.00 |
|  | lb/Day | 126.35 | 505.40 | 1263.51 |
| Selenium | ug/L | 1515.00 | 6060.00 | 15150.00 |
|  | lb/Day | 379.05 | 1516.21 | 3790.53 |
| Silver | ug/L | 29.45 | 165.80 | 438.50 |
|  | lb/Day | 7.37 | 41.48 | 109.71 |
| Zinc | ug/L | 1220.00 | 7280.00 | 19400.00 |
|  | lb/Day | 305.24 | 1821.46 | 4853.88 |
| Cyanide5 | mg/L | 0.10 | 0.40 | 1.01 |
|  | lb/Day | 25.27 | 101.08 | 252.70 |
| Total Chlorine Residual6 | mg/L | 202.00 | 808.00 | 6060.00 |
|  | lb/Day | 50540.40 | 202161.60 | 1516212.00 |
| Ammonia (as N) | mg/L | 60600.00 | 242400.00 | 606000.00 |
|  | lb/Day | 15162120.00 | 60648480.00 | 151621200.00 |
| Chronic Toxicity | TUc |  | 101 |  |
| Phenolic Compounds | mg/L | 3.03 | 12.12 | 30.30 |
|  | lb/Day | 758.11 | 3032.42 | 7581.06 |
| Chlorinated phenolics | mg/L | 0.10 | 0.40 | 1.01 |
|  | lb/Day | 25.27 | 101.08 | 252.70 |

c.	Effluent Limitations for Toxic, Non-carcinogenic Materials for Protection of Human Health3

d.	Effluent Limitations for Toxic, Carcinogenic Materials for Protection of Human Health3

mg/L	=		milligrams per liter

ug/L		=		micrograms per liter

ng/L		=		nanograms per liter

pg/L		= 		picograms per liter

mL/L 	= 		milliliters per liter

NTU 	= 		Nephelometric Turbidity Units

TUa 		= 		toxic units acute

TUc 		= 		toxic units chronic

lb/Day 	= 		pounds per day

3..	Any significant change in waste flow shall be cause for reevaluating effluent quality requirements.

4.	The 30-day average percent removal of CBOD5 and the 30-day average percent removal of TSS shall each not be less than 85 percent.

5.	Waste management systems that discharge to the ocean must be designed and operated in a manner that will maintain the indigenous marine life and a healthy and diverse marine community.

6.	Waste discharged through the SERRA Ocean Outfall must be essentially free of:

a.	Material that is floatable or will become floatable upon discharge.

b.	Settleable material or substances that form sediments which degrade benthic communities or other aquatic life.

c.	Substances which will accumulate to toxic levels in marine waters, sediments or biota.

d.	Substances that significantly decrease the natural light to benthic communities and other marine life.

e.	Materials that result in aesthetically undesirable discoloration of the ocean surface.

7.	Waste discharged through the SERRA Ocean Outfall shall be discharged in a manner that provides sufficient initial dilution to minimize the concentrations of substances not removed in treatment.

8.	Location of waste discharges must be determined after a detailed assessment of the oceanographic characteristics and current patterns to assure that:

a.	Pathogenic organisms and viruses are not present in areas where shellfish are harvested for human consumption or in areas used for swimming or other body-contact sports.

b.	Natural water quality conditions are not altered in areas designated as being of special biological significance or areas that existing marine laboratories use as a source of seawater.

c.	Maximum protection is provided to the marine environment.

Waste that contains pathogenic organisms or viruses should be discharged a sufficient distance from shellfishing and water-contact sports areas to maintain applicable bacterial standards without disinfection.  Where conditions are such that an adequate distance cannot be attained, reliable disinfection in conjunction with a reasonable separation of the discharge point from the area of use must be provided.  Disinfection procedures that do not increase effluent toxicity and that constitute the least environmental and human hazard shall be used.

9.	All waste treatment, containment and disposal facilities shall be protected against 100-year peak stream flows as defined by the Orange County flood control agency.

10.	All waste treatment, containment and disposal facilities shall be protected against erosion, overland runoff and other impacts resulting from a 100-year frequency 24-hour storm.

11.	Collected screenings, sludges, and other solids removed from liquid wastes shall be disposed of in a manner approved by the Regional Board Executive Officer (hereinafter Executive Officer).

12.	The discharge of substances for which effluent limitations are not established by this Order shall be prevented or, if the discharge cannot be prevented, minimized.

C.	RECEIVING WATER LIMITATIONS

1.	The discharge of waste through the SERRA Outfall shall not, by itself or jointly with any other discharge, cause violation of the following Ocean Plan ocean water quality objectives.  Compliance with the water quality objectives shall be determined from samples collected at stations representative of the area within the waste field where initial dilution is completed.

a.	Bacterial Characteristics

(1)	Water-Contact Standards

Within a zone bounded by the shoreline and a distance of 1,000 feet from the shoreline or the 30-foot depth contour, whichever is further from the shoreline, and in areas outside this zone used for water-contact sports, as determined by the Regional Board, but including all kelp beds, the following bacterial objectives shall be maintained throughout the water column:

(a)	Samples of water from each sampling station shall have a density of total coliform organisms less than 1,000 per 100 ml (10 per ml); provided that not more than 20 percent of the samples at any sampling station, in any 30-day period, may exceed 1,000 per 100 ml (10 per ml), and provided further that no single sample when verified by a repeat sample taken within 48 hours shall exceed 10,000 per 100 ml (100 per ml).

(b)	The fecal coliform density based on a minimum of not less than five samples for any 30-day period, shall not exceed a geometric mean of 200 per 100 ml nor shall more than 10 percent of the total samples during any 60-day period exceed 400 per 100 ml.

The "Initial Dilution Zone" of wastewater outfalls shall be excluded from designation as kelp beds for purposes of bacterial standards.  Adventitious assemblages of kelp plants on waste discharge structures (e.g., outfall pipes and diffusers) do not constitute kelp beds for purposes of bacterial standards.  Kelp beds, for the purpose of the bacterial standards of this Order, are significant aggregations of marine algae of the genera Macrocystis and Nereocystis.  Kelp beds include the total foliage canopy of Macrocystis and Nereocystis plants throughout the water column.

(2)	Shellfish Harvesting Standards

(a)	At all areas where shellfish may be harvested for human consumption, as determined by the Regional Board, the following bacterial objectives shall be maintained throughout the water column:

(b)	The median total coliform density shall not exceed 70 per 100 ml, and not more than 10 percent of the samples shall exceed 230 per 100 ml.

b.	Bacterial Assessment and Remedial Action Requirements

The requirements listed below shall be used to 1) determine the occurrence and extent of any impairment of a beneficial use due to bacterial contamination; 2) generate information which can be used in the development of an enterococcus standard; and 3) provide the basis for remedial actions necessary to minimize or eliminate any impairment of a beneficial use.

Measurement of enterococcus density shall be conducted at all stations where measurement of total and fecal coliforms are required.  In addition to the requirements of Receiving Water Limitation C.1.a of this Order, if a shore station consistently exceeds a coliform objective or exceeds a geometric mean enterococcus density of 24 organisms per 100 ml for a 30-day period or 12 organisms per 100 ml for a six-month period, the Regional Board shall require the discharger to conduct or participate in a survey to determine the source of the contamination.  The geometric mean shall be a moving average based on no less than five samples per month, spaced evenly over the time interval.  When a sanitary survey identifies a controllable source of indicator organisms associated with a discharge of sewage, the Regional Board may require the discharger and any other responsible parties identified by the Regional Board to take action to control the source.

c.	Physical Characteristics

(1)		Floating particulates and grease and oil shall not be visible.

(2)		The discharge of waste shall not cause aesthetically undesirable discoloration of the ocean surface.

(3)		Natural light shall not be significantly reduced at any point outside the initial dilution zone as a result of the discharge of waste.

(4)		The rate of deposition of inert solids and the characteristics of inert solids in ocean sediments shall not be changed such that benthic communities are degraded.

d.	Chemical Characteristics

(1)		The dissolved oxygen concentration shall not at any time be depressed more than 10 percent from that which occurs naturally, as a result of the discharge of oxygen-demanding waste materials.

(2)		The pH shall not be changed at any time more than 0.2 units from that which occurs naturally.

(3)		The dissolved sulfide concentration of waters in and near sediments shall not be significantly increased above that present under natural conditions.

(4)		The concentration of substances, set forth in Receiving Water Limitation C.3 of this Order, in marine sediments shall not be increased to levels which would degrade indigenous biota.

(5)		The concentration of organic materials in marine sediments shall not be increased to levels that would degrade marine life.

(6)		Nutrient materials shall not cause objectionable aquatic growths or degrade indigenous biota.

e.	Biological Characteristics

(1)		Marine communities, including vertebrate, invertebrate, and plant species, shall not be degraded.

(2)		The natural taste, odor, and color of fish, shellfish, or other marine resources used for human consumption shall not be altered.

(3)		The concentration of organic materials in fish, shellfish, or other marine resources used for human consumption shall not bioaccumulate to levels that are harmful to human health.

f.	Radioactivity

Discharge of radioactive waste shall not degrade marine life.

2.	The discharge of waste through the SERRA Ocean Outfall shall not, by itself or jointly with any other discharge, cause violation of the following Basin Plan ocean water quality objectives:

a.	The mean annual dissolved oxygen concentration shall not be less than 7.0 mg/L nor shall the minimum dissolved oxygen concentration be reduced below 5.0 mg/L at any time.

b.	The pH value shall not be depressed below 7.0 nor raised above 8.6.

3.	Toxic Materials

The discharge through the SERRA Ocean Outfall shall not by itself or jointly with any other discharge, cause the following Ocean Plan water quality objectives to be exceeded in the receiving water upon completion of initial dilution, except that limitations indicated for radioactivity shall apply directly to the undiluted waste effluent.

a.	Water Quality Objectives for the Protection of Marine Aquatic Life

| Constituent | Units | 6 Month Median | Daily Maximum | Instantaneous Maximum |
| --- | --- | --- | --- | --- |
| arsenic | ug/L | 8 | 32 | 80 |
| cadmium | ug/L | 1 | 4 | 10 |
| chromium (hexavalent) | ug/L | 2 | 8 | 20 |
| copper | ug/L | 3 | 12 | 30 |
| lead | ug/L | 2 | 8 | 20 |
| mercury | ug/L | 0.04 | 0.16 | 0.4 |
| nickel | ug/L | 5 | 20 | 50 |
| selenium | ug/L | 15 | 60 | 150 |
| silver | ug/L | 0.45 | 1.8 | 4.5 |
| zinc | ug/L | 20 | 80 | 200 |
| cyanide | ug/L | 1 | 4 | 10 |
| total chlorine residual | ug/L | 2 | 8 | 60 |
| ammonia (as N) | ug/L | 600 | 2,400 | 6,000 |
| chronic toxicity | TUc | -- | 1 | -- |
| phenolic compounds (non-chlorinated) | ug/L | 30 | 120 | 300 |
| chlorinated phenolics | ug/L | 1 | 4 | 10 |
| Endosulfan7 | ug/L | 0.009 | 0.018 | 0.027 |
| endrin | ug/L | 0.002 | 0.004 | 0.006 |
| HCH8 | ug/L | 0.004 | 0.008 | 0.012 |
| Radioactivity9 | Not to exceed limits specified in Title 17, Division 1, Chapter 5, Subsection 4, Group 3, Article 1, Section 30253 of the California Code of Regulations. |  |  |  |  |  |  |

b.	Water Quality Objectives for the Protection of Human Health -- Noncarcinogens

| Chemical | Units | 30-Day Average |
| --- | --- | --- |
| acrolein | ug/L | 220 |
| antimony | ug/L | 1,200 |
| bis(2-chloroethoxy)methane | ug/L | 4.4 |
| bis(2-chloroisopropyl)ether | ug/L | 1,200 |
| chlorobenzene | ug/L | 570 |
| chromium (III) | ug/L | 190,000 |
| di-n-butyl phthalate | ug/L | 3,500 |
| Dichlorobenzenes10 | ug/L | 5,100 |
| 1,1-dichloroethylene | ug/L | 7,100 |
| diethyl phthalate | ug/L | 33,000 |
| dimethyl phthalate | ug/L | 820,000 |
| 4,6-dinitro-2-methylphenol | ug/L | 220 |
| 2,4-dinitrophenol | ug/L | 4.0 |
| ethylbenzene | ug/L | 4,100 |
| fluoranthene | ug/L | 15 |
| hexachlorocyclopentadiene | ug/L | 58 |
| isophorone | ug/L | 150,000 |
| nitrobenzene | ug/L | 4.9 |
| thallium | ug/L | 14 |
| toluene | ug/L | 85,000 |
| 1,1,2,2-tetrachloroethane | ug/L | 1,200 |
| tributyltin | ug/L | 0.0014 |
| 1,1,1-trichloroethane | ug/L | 540,000 |
| 1,1,2-trichloroethane | ug/L | 43,000 |

c.	Water Quality Objectives for the Protection of Human Health -- Carcinogens

| Chemical | Units | 30-Day Average |
| --- | --- | --- |
| acrylonitrile | ug/L | 0.10 |
| aldrin | ug/L | 0.000022 |
| benzene | ug/L | 5.9 |
| benzidine | ug/L | 0.000069 |
| beryllium | ug/L | 0.033 |
| bis(2-chloroethyl)ether | ug/L | 0.045 |
| bis(2-ethylhexyl)phthalate | ug/L | 3.5 |
| carbon tetrachloride | ug/L | 0.90 |
| chlordane11 | ug/L | 0.000023 |
| chloroform | ug/L | 130 |
| DDT12 | ug/L | 0.00017 |
| 1,4-dichlorobenzene | ug/L | 18 |
| 3,3-dichlorobenzidine | ug/L | 0.0081 |
| 1,2-dichloroethane | ug/L | 130 |
| dichloromethane | ug/L | 450 |
| 1,3-dichloropropene | ug/L | 8.9 |
| dieldrin | ug/L | 0.00004 |
| 2,4-dinitrotoluene | ug/L | 2.6 |
| 1,2-diphenylhydrazine | ug/L | 0.16 |
| Halomethanes13 | ug/L | 130 |
| Heptachlor14 | ug/L | 0.00072 |
| hexachlorobenzene | ug/L | 0.00021 |
| hexachlorobutadiene | ug/L | 14 |
| hexachloroethane | ug/L | 2.5 |
| N-nitrosodimethylamine | ug/L | 7.3 |
| N-nitrosodiphenylamine | ug/L | 2.5 |
| PAHs15 | ug/L | 0.0088 |
| PCBs16 | ug/L | 0.000019 |
| TCDD equivalents17 | pg/L | 0.0039 |
| tetrachloroethylene | ug/L | 99 |
| toxaphene | ug/L | 0.00021 |
| trichloroethylene | ug/L | 27 |
| 2,4,6-trichlorophenol | ug/L | 0.29 |
| vinyl chloride | ug/L | 36 |

mg/L = milligrams per liter

ug/L = micrograms per liter

ng/l = nanograms per liter

pg/l = picograms per liter

NTU = Nephelometric Turbidity Unit

TUc = toxic units chronic

# D.	PRETREATMENT REQUIREMENTS

- The discharger shall be responsible and liable for the performance of  all pretreatment requirements contained in 40 CFR Part 403, including any subsequent revisions to 40 CFR Part 403.  Where 40 CFR Part 403 or subsequent revisions place mandatory actions upon the discharger, but do not specify a timetable for completion, the discharger shall complete the mandatory actions within six months of the issuance date of this Order, or the effective date of the 40CFR403 revisions, whichever comes later. For violations of pretreatment requirements, the discharger shall be subject to enforcement actions, penalties, fines, and other remedies by the USEPA, and/or the Regional Board, as provided in the CWA and/or the Porter-Cologne Water Quality Control Act (CWC).

- The discharger shall implement and enforce its approved pretreatment program, and all subsequent revisions, which are hereby made an enforceable condition of this Order. The discharger shall enforce the requirements promulgated under Sections 307(b), 307(c), 307(d), and 402(b) of the CWA with timely, appropriate, and effective enforcement actions.  The discharger shall cause industrial users subject to federal categorical standards to achieve compliance no later than the date specified in those requirements, or in the case of a new industrial user, upon commencement of the discharge.

3.	The discharger shall perform the pretreatment functions as required in 40CFR403 including, but not limited to:

- Implement the necessary legal authorities as provided in 40CFR403.8(f)(1);

- Enforce the pretreatment requirements under 40CFR403.5 and 403.6;

- Implement the programmatic functions as provided in 40CFR403.8(f)(2); and

d.	Provide the requisite funding and personnel to implement the pretreatment program as provided in 40CFR403.8(f)(3).

4.	By March 1st of each year, the discharger shall submit an annual report to the Regional Board; the USEPA Region 9; the State Water Resources Control Board, Division of Water Quality, Regulations Unit; and the County of Orange Health Care Agency, Environmental Health Division, Hazardous Materials Division, describing its pretreatment activities over the previous calendar year.  In the event the discharger is not in compliance with any condition or requirement of this Order, or any pretreatment compliance inspection/audit requirements, the discharger shall include the reasons for noncompliance and state how and when it shall comply with such conditions and requirements. The annual report shall contain, but not be limited to, the following information:

a.	A summary of analytical results from representative flow-proportioned 24 hour composite sampling of the discharger’s influent and effluent for those pollutants known or suspected to be discharged by industrial users that the USEPA has identified under Section 307(a) of the CWA which are known or suspected to be discharged by industrial users. This will consist of an annual full priority pollutant scan.  Wastewater sampling and analysis shall be performed in accordance with the minimum frequency of analysis stated in the Monitoring and Reporting Program of this Order.  The discharger shall also provide influent and effluent monitoring data for nonpriority pollutants which the discharger believes may be causing or contributing to interference and/or pass through.  The discharger is not required to sample and analyse for asbestos. Sludge sampling and analysis is addressed in the sludge section of this Order. Wastewater sampling and analysis shall be performed in accordance with 40 CFR Part 136.

b.	A discussion of upset, interference, or pass through, if any, at the  POTW’s which the discharger knows or suspects were caused by industrial users. The discussion shall include the reasons why the incidents occurred, any corrective actions taken, and, if known, the name and  address of the industial user(s) responsible. The discussion shall also include a review of the applicable local pollutant limitations to determine whether any additional; limitations or changes to existing limitations, are necessary to prevent  pass through, interference, or noncompliance with sludge disposal requirements.

c.	An updated list of the dischargers significant industrial users including their names and addresses, and showing a list of additions, deletions, or name changes keyed to the previous submitted list.  The list shall identify the industrial users subject to federal categorical standards by specifying which standards are applicable.  The list shall also indicate which significant (non-categorical) industrial users are subject to local limitations.

d.	The discharger shall characterize the compliance status of each significant industrial user (SIU) by providing a list or table for the following:

- Name of SIU and category if subject to categorical standards;

- Type of  wastewater treatment or control processes in place;

- Number of samples taken by SIU during the year;

- Number of samples and inspections by discharger during the year;

- For an SIU subject to discharge requirements for total toxic organics(TTO), whether all required certifications were provided;

- A list of pretreatment standards (categorical or local) violated during the year, or any other violations;

- Industries in significant noncompliance(SNC) as defined at 40 CFR Part 403.12(f)(2)(vii)  at any time during the year;

- A summary of enforcement actions or any other actions taken against SIU(s) during the year.  Describe the type of action, final compliance date, and the amount of fines and/or penalties collected, if any. Describle any proposed actions for bringing an SIU into compliance; and

- The name(s) of any SIU(s) required to submit a baseline monitoring report (BMR), and any SIU’s currently discharging under a BMR.

e.	A brief description of any programs the discharger implements to reduce pollutants from industrial users not classified as SIU’s;

f.	A brief description of any significant changes in operating the pretreatment program which differ from the previous year including, but not limited to, changes in the program’s administraative structure, local limits, monitoring program, legal authority, enforcement policy, and funding and staffing levels;

g.	A summary of the annual pretreatment program budget, including the cost of pretreatment program functions and equipment purchases;

h.	A summary of activities to involve and inform the public of the pretreatment program including a copy of the newspaper notice, if any, required under 40CFR403.8(f)(2)(vii);

i.	A description of any changes in sludge disposal methods; and

j.	A discussion of any concerns not described elsewhere in the annual report.

5.	The discharger shall submit a semi-annual SIU compliance status report to the Regional Board, the State Water Resources Control Board, and the USEPA.  The report shall cover the period of January 1 through June 30, and shall be submitted no later than September 1st. The report shall identify:

a.	The names and addresses of all SIU’s which violated any discharge or reporting requirements during the semi-annual reporting period;

b.	A description of the violations including whether the discharge violations were for categorical standards or local limits;

c.	A description of the enforcement actions, or other actions taken to remedy the noncompliance; and

d.	The status of active enforcement actions, or other actions taken in response to SIU noncompliance identified in previous reports.

6.	The discharger shall continue with its implementation of a Nonindustrial SourceControl Program consisting of a public education program designed to minimize the entrance of nonindustrial toxic pollutants and pesticides into the sanitary sewer system. The Program shall be reviewed periodically and addressed in the annual report.

E.	SLUDGE REQUIREMENTS

1.	Management of all solids and sludge must comply with all requirements of CFR Parts 257, 258, 501, and 503, including all monitoring, record-keeping, and reporting requirements.  Since the State of California, hence the Regional and State Boards, has not been delegated the authority by the USEPA to implement the sludge program, enforcement of sludge requirements of CFR Part 503 is under USEPA's jurisdiction.

2.	All solids and sludge must be disposed of in a municipal solid waste landfill, reused by land application, or disposed of in a sludge-only landfill in accordance with 40 CFR Parts 503 and 258, and Title 23 CCR Chapter 15.  If the discharger desires to dispose of solids or sludge by a different method, a request for permit modification must be submitted to the USEPA and this Regional Board 180 days prior to the alternative disposal.

3.	Sludge that is disposed of in a municipal solid waste landfill must meet the requirements of 40 CFR 25.  In the annual self-monitoring report, the discharger shall include the amount of sludge disposed of, and the landfill(s) to which it was sent.

4.	The permittee shall ensure that all biosolids produced at its facility are used or disposed of in compliance with the applicable portions of:

a.	40 CFR 503: for biosolids which are land applied (placed on the land for the purpose of providing nutrients or conditioning the soil for crops or vegetation), placed in surface disposal sites (placed on the land for the purpose of disposal), stored, or incinerated;

b.	40 CFR 258: for biosolids disposed in a municipal solid waste landfill;

c.	40 CFR 257: for other disposal practices.

The permittee is responsible for ensuring compliance with these regulations whether the permittee uses or disposes of the biosolids itself or contracts with another party for further treatment, use, or disposal.  The permittee is responsible for informing subsequent preparers, appliers, and disposers of the requirements that they must meet under 40 CFR 257, 258, and 503.

5.	Notification of non-compliance: The permittee shall notify EPA Region 9, the San Diego Regional Board, and the Regional Board where the biosolids are used or disposed of any non-compliance within 24 hours if the non-compliance may seriously endanger health or the environment.  For other instances of non-compliance, the permittee shall notify EPA Region 9 and the Regional Boards of the non-compliance in writing within 5 working days of becoming aware of the non-compliance.  See Attachment No. 5 for contact information.

6.	Inspection and Entry: The Regional Board, EPA, or an authorized representative, upon the presentation of credentials, shall be allowed by the permittee, directly or through contractual arrangements with the permittee’s biosolids contractors, a) to enter upon all premises where biosolids produced by the permittee are treated, stored, used, or disposed, b) to have access to and copy any records that must be kept under the conditions of this permit or of 40 CFR 503, and c) to inspect any facilities, equipment, or operations used by the permittee or its contractors in the production, treatment, storage, use, or disposal of the biosolids.

7.	The permittee shall submit an annual biosolids report to the EPA Region 9 Biosolids Coordinator and the Regional Board by February 19 of each year for the period covering the previous calendar year, with the following:

a.	The amount of biosolids generated that year, reported in dry metric tons, and the amount accumulated from previous years;

b.	The results of all pollutant and pathogen monitoring (Results shall be reported on a 100% dry weight basis for comparison with 40 CFR 503 limits.  Any sample results reported on a wet weight basis must report the % solids of that sample.);

c.	Descriptions of methods used to achieve pathogen reduction and vector attraction reduction, including supporting time and temperature data, and certifications required in 40 CFR 503.17 and 503.27;

d.	Names and addresses of entities receiving biosolids for further treatment, use or disposal, and volumes of biosolids sent to each;

e.	For all biosolids used or disposed at the permittee's facilities, the site and management practice information and certification required in 40 CFR 503.17 and 503.27; and

f.	For all biosolids temporarily stored, the information required in 40 CFR 503.20 required to demonstrate temporary storage.

g.	Reports shall be submitted to:

(1)	Regional Biosolids Coordinator

US EPA (WTR-7)

75 Hawthorne St.

San Francisco, CA 94105-3901

(2)	Executive Officer

California Regional Water Quality Control Board

San Diego Region

9771 Clairemont Mesa Boulevard, Suite A

San Diego, California  92124-1324

Phone - (858) 467-2952

Fax - (858) 571-6972

8.	All the requirements of 40 CFR 503 and 23 CCR 15 are enforceable by the USEPA and this Regional Board whether or not the requirements are stated in an NPDES permit or any other permit issued to the discharger.

9.	The discharger shall take all reasonable steps to prevent and minimize any sludge use or disposal in violation of this Order that has a likelihood of adversely affecting human health or the environment.

10.	Solids and sludge treatment, storage, and disposal or reuse shall not create a nuisance, such as objectionable odors or flies, and shall not result in groundwater contamination.

11.	The solids and sludge treatment and storage site shall have facilities adequate to divert surface water runoff from adjacent areas, to protect the boundaries of the site from erosion, and to prevent drainage from the treatment and storage site.  Adequate protection is defined as protection from at least a 100-year storm and protection from the highest possible tidal stage that may occur.

12.	The discharge of sewage sludge and solids shall not cause waste material to be in a position where it is, or can be, conveyed from the treatment and storage sites and deposited in the waters of the state.

- The discharger shall submit an annual report to the USEPA and this Regional Board containing monitoring results and pathogen and vector attraction reduction requirements, as specified by 40 CFR 503.  The discharger shall also report the quantity of sludge disposed and the disposal method.  This self-monitoring report must be postmarked by February 1 of each year and report for the period covering the previous calendar year.

F.	PROVISIONS

1.	The discharger must comply with all conditions of this Order.  Any permit noncompliance constitutes a violation of the CWA and the California Water Code, and is grounds for enforcement action; for permit termination, revocation and reissuance, or modification; or for denial of an application for permit renewal, modification, or reissuance.

2.	The discharger must comply with all standard provisions, where applicable, as stated in 40 CFR 122.41 (see Attachment No. 3) and Standard Provisions (Attachment No. 4).

3.	Neither the treatment nor the discharge of waste shall create a pollution, contamination, or nuisance as defined by Section 13050 of the California Water Code.

4.	The following sections of 40 CFR (see Attachment No. 5) are incorporated into this permit by reference, and the discharger must comply with these provisions:

a.	122.5:  	Effect of a permit

b.	122.21:	Application for a permit

c.	122.22:	Signatories to permit applications and reports

d.	122.41:	Conditions applicable to all permits

e.	122.61:	Transfer of permits

f.	122.62:	Modification or revocation of permits

g.	122.63:	Minor modifications of permits

h.	122.64:	Termination of permits

5.	This Order may be modified, revoked and reissued, or terminated for causes including, but not limited to, the following:

a.	Violation of any terms or conditions of this Order.

b.	Obtaining this Order by misrepresentation or failure to disclose fully all relevant facts.

c.	A change in any condition that requires either a temporary or permanent reduction or elimination of the authorized discharge.

The filing of a request by the discharger for modification, revocation and reissuance, or termination of this Order, or a notification of planned change in or anticipated noncompliance with this Order does not stay any condition of this Order.

6.	If any applicable toxic effluent standard or prohibition (including any schedule of compliance specified in such effluent standard or prohibition) is promulgated under Section 307(a) of the CWA for a toxic pollutant and that standard or prohibition is more stringent than any limitation on the pollutant in this Order, the Executive Officer may institute proceedings under these regulations to modify or revoke and reissue the Order to conform to the toxic effluent standard or prohibition.

7.	The discharger shall comply with effluent standards or prohibitions established under Section 307(a) of the CWA for toxic pollutants and with standards for sewage sludge use and disposal established under Section 405(d) of the CWA within the time provided in the regulations that establish those standards or prohibitions or standards for sewage sludge use or disposal, even if this Order has not yet been modified to incorporate the requirement.

8.	The discharger shall comply with all existing federal and state laws and regulations that apply to its sewage sludge use and disposal practice(s), and with the CWA Section 405(d) and 40 CFR Part 257.

9.	The discharger shall allow the Regional Board, or any Regional Board authorized representative, or any authorized representative of the USEPA (including an authorized contractor acting as a representative of the Regional Board or USEPA),  upon the presentation of credentials and other documents as may be required by law, to:

a.	Enter upon the discharger's premises where a regulated facility or activity is located or conducted, including sludge use and disposal activities, or where records must be kept under the conditions of this Order;

b.	Have access to and copy, at reasonable times, any records that must be kept under the conditions of this Order;

c.	Inspect at reasonable times any facilities, equipment (including monitoring and control equipment), practices or operations regulated or required under this Order including sludge use and disposal sites; and

d.	Sample or monitor at reasonable times, for the purposes of assuring compliance with this Order or as otherwise authorized by the CWA or California Water Code, any substances or parameters at any location.

10.	This Order does not convey any property rights of any sort or any exclusive privilege.  The requirements prescribed herein do not authorize the commission of any act causing injury to persons or property, nor protect the discharger from its liabilities under federal, state, or local laws, nor create a vested right for the discharger to continue its waste discharge.

11.	It shall not be a defense for the discharger in an enforcement action that it would have been necessary to halt or reduce the permitted activity in order to maintain compliance with the conditions of this Order.  Upon reduction, loss, or failure of a treatment facility, the discharger shall, to the extent necessary to maintain compliance with this Order, control all discharges until the facility is restored or an alternative method of treatment is provided.  This provision applies, for example, when the primary source of power of a treatment facility fails, is reduced, or is lost.

12.	Supervisors and operators of the discharger's wastewater treatment facilities shall possess a certificate of appropriate grade in accordance with Chapter 14 of Division 4 of Title 23 of the California Code of Regulations.

13.	The discharger shall, at all times, properly operate and maintain all facilities and systems of treatment and control including sludge use and disposal facilities (and related appurtenances) which are installed or used by the discharger to achieve compliance with the conditions of this Order.  Proper operation and maintenance also includes adequate laboratory controls and appropriate quality assurance procedures.  This provision requires the operation of back-up or auxiliary facilities or similar systems which are installed by the discharger only when the operation is necessary to achieve compliance with the conditions of this Order.

14.	The discharger's wastewater treatment facilities shall be operated and maintained in accordance with the operation and maintenance manual(s) prepared by the discharger through the Clean Water Grant Program.

15.	A copy of this Order shall be posted at a prominent location at or near the treatment and disposal facilities, and shall be available to operating personnel at all times.

16.	The discharger shall comply with any interim effluent limitations as established by an addendum, enforcement action or revised waste discharge requirements which have been or may be adopted by this Regional Board.

- All proposed new treatment facilities and expansions of existing treatment facilities shall be completely constructed and operable prior to initiation of the discharge from the new or expanded facilities.

a.	The discharger shall submit a certification report for each new treatment facility, expansion of an existing treatment facility, and re-rating of an existing treatment facility.  For new treatment facilities and expansions, the certification report shall be prepared by the design engineer.  For re-ratings, the certification report shall be prepared by the engineer who evaluated the treatment facility capacity.  The certification report shall:

(1)	Identify the design capacity of the treatment facility;

(2)	Certify the adequacy of each component of the treatment facility; and

(3)	Contain a requirement-by-requirement analysis, based on acceptable engineering practices, of how the process and physical design of the facility will ensure compliance with this Order.

b.	The signature and engineering license number of the engineer preparing the certification report shall be affixed to the report.  The certification report, should, if possible, be submitted prior to beginning construction.  The discharger shall not initiate a discharge from a new treatment facility or initiate a discharge from an existing treatment facility at a 30-day average dry weather flowrate in excess of its previously approved design capacity until:

(1).	The certification report is received by the Executive Officer;

(2)	The Executive Officer has received written notification of the completion of construction (new treatment facilities and expansions only);

(3)	An inspection of the plant has been made by the Regional Board staff (new treatment facilities and expansions only); and

(4).	The Executive Officer has provided the discharger with written authorization to discharge at a 30-day average dry weather flowrate not to exceed the revised design capacity.

18.	The discharger shall take all reasonable steps to minimize or prevent any discharge or sludge use or disposal in violation of this Order which has a reasonable likelihood of adversely affecting human health or the environment.

19.	If only one sample is collected during the time period associated with the effluent limitations (e.g., 30-day average or 6-month median), the single measurement shall be used to determine compliance with the effluent limitation for the entire time period.

20.	All analytical data shall be reported uncensored with detection limits and quantitation limits identified.  For any effluent limitation, compliance shall be determined using appropriate statistical methods to evaluate multiple samples.  Sufficient sampling and analysis shall be conducted to determine compliance.

21.	Compliance based on a single sample analysis shall be determined where appropriate as described below.

a.	When a calculated effluent limitation is greater than or equal to the PQL (defined below), compliance shall be determined based on the calculated effluent limitation and either single or multiple sample analyses.

b.	When the calculated effluent limitation is below the PQL, compliance determinations based on analysis of a single sample shall only be undertaken if the concentration of the constituent of concern in the sample is greater than or equal to the PQL.

c.	When the calculated effluent limitation is below the PQL and recurrent analytical responses between the PQL and the calculated limit occur, compliance shall be determined by statistical analysis of multiple samples.

22.	Published values for MDLs (defined below) and PQLs should be used except where revised MDLs and PQLs are available from recent laboratory performance evaluations, in which case the revised MDLs and PQLs should be used.  Where published values are not available, the Executive Officer will determine appropriate values based on available information, including information submitted by the discharger upon request of the Executive Officer.

a.	The Method Detection Limit (MDL) is the minimum concentration of a substance that can be measured and reported with 99% confidence that the analyte concentration is greater than zero, as defined in 40 CFR Part 136 Appendix B.

b.	The Practical Quantitation Level (PQL) is the lowest concentration of a substance which can be consistently determined within +/-20% of the true concentration by 75% of the labs tested in a performance evaluation study.  Alternatively, if performance data are not available, the PQL for carcinogens is the MDL x 5, and for noncarcinogens is the MDL x 10.

23.	When determining compliance based on a single sample, with a single effluent limitation which applies to a group of chemicals (e.g., PCBs) concentrations of individual members of the group may be considered to be zero if the analytical response for individual chemicals falls below the MDL for that parameter.

24.	The 6-month median effluent concentration limitation shall apply as a moving median of daily values for any 180-day period in which daily values represent flow-weighted average concentrations within a 24-hour period.  For intermittent discharges, the daily value shall be considered to equal zero for days on which no discharge occurred.  The 6-month median receiving water limitation shall apply as a moving median of all values collected for any 180-day period.

25.	The 30-day average effluent limitation shall be the moving arithmetic mean of daily concentrations over the specified 30-day period.

26.	The 7-day average shall be the moving arithmetic mean of daily concentrations over the specified 7-day period.

27.	The daily maximum effluent limitation shall apply to flow-weighted 24-hour composite samples.  The daily maximum receiving water limitation shall apply to grab sample determinations.

28.	The instantaneous maximum effluent limitation shall apply to grab sample determinations.  The instantaneous maximum receiving water limitation shall apply to grab sample determinations.

29.	The mass emission rate (MER), in pounds per day, shall be obtained from the following calculation for any calendar day:

mass emission rate (lb/Day) = 8.34 x Q x C

in which Q and C are the flow rate in MGallons/ Day and the constituent concentration in mg/L, respectively, and 8.34 is a conversion factor with units of [lb/MGallons] / [mg/L].  If a composite sample is taken, then C is the concentration measured in the composite sample and Q is the average flow rate occurring during the period over which the samples are composited.

30.	Compliance with the Acute Toxicity limitation in Discharge Specification B.1.a. of this Order shall be determined using an established protocol, e.g., American Society for Testing Materials (ASTM), USEPA, American Public Health Association, or State Board.  Acute Toxicity (TUa) shall be expressed in Toxic Units Acute (TUa), where:

TUa =        100

96-hour LC50

Where LC50 (Lethal Concentration 50%) is the percent waste giving 50% survival of test organisms.  LC50 shall be determined by static or continuous flow bioassay techniques using standard test species.  If specific identifiable substances in wastewater can be demonstrated by the discharger as being rapidly rendered harmless upon discharge to the marine environment, but not as a result of dilution, the LC50 may be determined after the test samples are adjusted to remove the influence of those substances.

When it is not possible to measure the 96-hour LC50 due to greater than 50% survival of the test species in 100% waste, the toxicity concentration shall be calculated by the following:

TUa = log (100 - S)

1.7

where S is the percentage survival in 100% waste.  If S > 99, TUa shall be reported as zero.

31.	Compliance with the Chronic Toxicity effluent limitation established in Discharge Specification No. B.1.b of this Order shall be determined using critical life stage toxicity tests.  Chronic Toxicity (TUc) shall be expressed as Toxic Units Chronic (TUc), where:

TUc =    100

NOEL

where NOEL is the No Observed Effect Level and is expressed as the maximum percent effluent that causes no observable effect on a test organism, as determined by the result of a critical life stage toxicity test listed below.

A minimum of three test species with approved test protocols shall be used to measure compliance with the chronic toxicity objective.  If possible, the test species shall include a fish, an invertebrate, and an aquatic plant.  After a screening period, monitoring may be reduced to the most sensitive species.  Dilution and control water should be obtained from an unaffected area of the receiving waters.  The sensitivity of the test organisms to a reference toxicant shall be determined concurrently with each bioassay test and reported with the test results.

The tests specified in the July 1997 Ocean Plan shall be used to measure TUc.  Other tests may be added to the list when approved by the SWRCB.

32.	If toxicity testing results show a violation of any acute or chronic toxicity limitation identified in Discharge Specification B.1 of this Order, the discharger shall:

a.	Take all reasonable measures necessary to immediately minimize toxicity; and

b.	Increase the frequency of the toxicity test(s) that showed a violation to at least two times per month until the results of at least two consecutive toxicity tests do not show violations.

If the Executive Officer determines that toxicity testing shows consistent violation of any acute or chronic toxicity limitation identified in Discharge Specification B.1. of this Order, the discharger shall conduct a Toxicity Reduction Evaluation (TRE) which includes all reasonable steps to identify the source of toxicity.  Once the source of toxicity is identified, the discharger shall take all reasonable steps to reduce the toxicity to meet the toxicity limitations identified in Discharge Specification B.1 of this Order.

Within fourteen days of completion of the TRE, the discharger shall submit the results of the TRE, including a summary of the findings, data generated, a list of corrective actions necessary to achieve consistent compliance with all the toxicity limitations of this Order and prevent recurrence of violations of those limitations, and a time schedule for implementation of such corrective actions.  The corrective actions and time schedule shall be modified at the direction of the Executive Officer.

33.	For all bacterial analyses, sample dilutions should be performed so the range of values extends from 2 to 16,000 MPN (most probable number).  The detection methods used for each analysis shall be reported with the results of the analysis.  Detection methods used for coliforms (total and fecal) shall be those presented in the most recent edition of Standard Methods for the Examination of Water and Wastewater or any improved method determined by the Regional Board (and approved by USEPA) to be appropriate.  Detection methods used for enterococcus shall be those presented in USEPA publication USEPA 600/4-85/076, Test Methods for Escherichia coli and Enterococci in Water By Membrane Filter Procedure or any improved method determined by the Regional Board to be appropriate.

34.	The geometric mean used for determining compliance with bacterial standards is calculated with the following equation:

Geometric Mean = (C1 x C2 x ... x Cn) 1/n

where n is the number of days samples were collected during the period and C is the concentration of bacteria (MPN/100 mL) found on each day of sampling.

35.	As used in this Order, waste includes a discharger's total discharge, of whatever origin (i.e. gross, not net, discharge).

36.	Bypass of Treatment Facilities

a.	Definitions

(1)	"Bypass" means the intentional diversion of waste streams from any portion of a treatment facility.

(2)	"Severe property damage" means substantial physical damage to property, damage to the treatment facilities which causes them to become inoperable, or substantial and permanent loss of natural resources which can reasonably be expected to occur in the absence of a bypass.  Severe property damage does not mean economic loss caused by delays in production.

b.	Bypass not Exceeding Limitations

The discharger may allow any bypass to occur which does not cause effluent limitations of this Order or the concentrations of pollutants set forth in Ocean Plan Table A or Table B to be exceeded, but only if it also is for essential maintenance to assure efficient operation.  These bypasses are not subject to the provisions of paragraphs c. and d. of this provision.

c.	Notice

(1)	Anticipated bypass.  If the discharger knows in advance of the need for a bypass, it shall submit prior notice, if possible, at least ten days before the date of the bypass.

(2)	Unanticipated bypass.  The discharger shall submit notice of an unanticipated bypass as required in Reporting Requirement G.10 of this Order.

d.	Prohibition of Bypass

(1)	Bypass is prohibited and the Regional Board may take enforcement action against the discharger for bypass, unless:

(a)	Bypass was unavoidable to prevent loss of life, personal injury, or severe property damage;

(b)	There were no feasible alternatives to the bypass, such as the use of auxiliary treatment facilities, retention of untreated wastes, or maintenance during normal periods of equipment downtime.  This condition is not satisfied if adequate back-up equipment should have been installed in the exercise of reasonable engineering judgment to prevent a bypass which occurred during normal periods of equipment downtime or preventive maintenance; and

(c)	The discharger submitted notices as required under paragraph c. of this provision.

(2)	The Executive Officer may approve an anticipated bypass, after considering its adverse effect, if the Executive Officer determines that it will meet the three conditions listed in paragraph d.(1) of this provision.

37.	Upset

a.	Definition

"Upset" means an exceptional incident in which there is unintentional and temporary noncompliance with technology based permit effluent limitations because of factors beyond the reasonable control of the discharger.  An upset does not include noncompliance to the extent caused by operational error, improperly designed treatment facilities, inadequate treatment facilities, lack of preventive maintenance, or careless or improper operation.

b.	Effect of an Upset

An upset constitutes an affirmative defense to an action brought for noncompliance with such technology-based permit effluent limitations if the requirements of paragraph c. of this provision are met.  No determination made during administrative review of claims that noncompliance was caused by upset, and before an action for noncompliance, is final administrative action subject to judicial review.

c.	Conditions Necessary for a Demonstration of Upset

A discharger who wishes to establish the affirmative defense of upset shall demonstrate, through properly signed, contemporaneous operating logs, or other relevant evidence that:

(1)	An upset occurred and that the discharger can identify the cause(s) of the upset;

(2)	The permitted facility was at the time being properly operated;

(3)	The discharger submitted notice of the upset as required in Reporting Requirement G.10 of this Order; and

(4)	The discharger complied with any remedial measures required under Provision F.18 of this Order.

d.	Burden of Proof

In any enforcement proceeding the discharger seeking to establish the occurrence of an upset has the burden of proof.

38.	The discharger shall maintain a Sewer Overflow Prevention Plan (SOPP) in an up-to-date condition and shall amend the SOPP whenever there is a change (e.g. in the design, construction, operation, or maintenance of the sewerage system or sewerage facilities) which materially affects the potential for sewer overflows.  The discharger shall review and amend the SOPP as appropriate after each sewer overflow from the SERRA Ocean Outfall and the area tributary to the SERRA Ocean Outfall..  The SOPP and any amendments thereto, shall be subject to the approval of the Executive Officer and shall be modified as directed by the Executive Officer.  The discharger shall submit the SOPP and any amendments thereto to the Executive Officer upon request of the Executive Officer.  The discharger shall ensure that the up-to-date SOPP is readily available to sewerage system personnel at all times and that sewerage system personnel are familiar with it.

39.	The discharger shall maintain a Sewer Overflow Response Plan (SORP) for the SERRA Ocean Outfall and the area tributary to the SERRA Ocean Outfall.  The SORP shall establish procedures for responding to sewer overflows from the SERRA Ocean Outfall and the area tributary to the SERRA Ocean Outfall so as to (a) minimize the sewer overflow volume which enters surface waters, and (b) minimize the adverse effects of sewer overflows on water quality and beneficial uses.  The discharger shall maintain the SORP in an up-to-date condition and shall amend the SORP as necessary to accomplish these objectives.  The discharger shall review and amend the SORP as appropriate after each sewer overflow from the SERRA Ocean Outfall and the area tributary to the SERRA Ocean Outfall.  The SORP, and any amendments thereto, shall be subject to the approval of the Executive Officer and shall be modified as directed by the Executive Officer.  The discharger shall submit the SORP and any amendments thereto to the Executive Officer upon request of the Executive Officer.  The discharger shall ensure that the up-to-date SORP is readily available to sewerage system personnel at all times and that sewerage system personnel are familiar with it.

40.	No later than 6 months after the adoption of this Order, the discharger shall submit a written report to the Executive Officer, addressing the following:

a.	Most current information on the capacity of the SERRA Ocean Outfall.

b.	The dischargers’ best estimate of when the average daily dry-weather flow will equal or exceed the SERRA Ocean Outfall capacity.

c.	The dischargers’ intended schedule for studies, design, and other steps needed to provide additional capacity for the SERRA Ocean Outfall and/or to control the flowrate before the flowrate is equal to the current outfall capacity.

d.	The report must be signed and agreed upon by each of the parties discharging to the SERRA Ocean Outfall.

G.	REPORTING REQUIREMENTS

1.	The discharger must comply with standard monitoring and reporting requirements, where applicable, as stated in 40 CFR 122.41 (see Attachment No. 3) and Standard Provisions (Attachment No. 4).

- This Order expires February 9, 2005.  If the discharger wishes to continue an activity regulated by this Order after the expiration date of this Order, the discharger must apply for and obtain new waste discharge requirements.  The discharger must submit a full and complete Report of Waste Discharge in accordance with Title 23 of the California Code of Regulations, to the Executive Officer, not later than 180 days in advance of the expiration date of this Order, as application for issuance of new waste discharge requirements.  Not less than 180 days prior to any material change in the character, location, volume, or amount of waste discharge, the Discharger shall submit a technical report describing such changes.  Such changes include but are not limited to the following:

a.	Addition of a major industrial waste discharge to a discharge of essentially domestic sewage, or the addition of a new process or product by an industrial facility resulting in a change in the character of the waste;

b.	Significant change in disposal method (e.g., change from land disposal to a direct discharge to water, or change in the method of treatment which would significantly alter the characteristics of the waste);

c.	Significant change in the disposal area (e.g., moving the discharge to another drainage area, to a different water body, or to a disposal area significantly removed from the original area potentially causing different water quality or nuisance problems);

d.	Increase in flow beyond that specified in the waste discharge requirements;

e.	Increase in area or depth to be used for solid waste disposal beyond that specified in the waste discharge requirements [CWC  13372, 13376, 13264, 23 CCR 2210];

f.	Any substantial change in the amount or characteristics of pollutants used, handled, stored, or generated;

g.	Any new discharge of pollutants or new potential pollutant source; and/or

h.	Other circumstances which could result in a material change in the character, amount, or location of discharges. [CWC  13372, 13264,23 CCR 2210]

3.	All applications, reports, or information submitted to the Executive Officer of this Regional Board shall be signed and certified.

a.	All Reports of Waste Discharge shall be signed by either a principal executive officer or ranking elected official.

b.	All reports required by this Order and other information requested by the Executive Officer shall be signed by a person described in paragraph a. of this reporting requirement, or by a duly authorized representative of that person.  A person is a duly authorized representative only if:

(1)	The authorization is made in writing by a person described in paragraph a. of this reporting requirement;

(2)	The authorization specifies either an individual or a position having responsibility for the overall operation of the regulated facility or activity such as the position of plant manager, operator of a well or a well field, superintendent, position of equivalent responsibility, or an individual or position having overall responsibility for environmental matters for the company (A duly authorized representative may thus be either a named individual or any individual occupying a named position.); and

(3)	The written authorization is submitted to the Executive Officer.

- If an authorization under paragraph b. of this reporting requirement is no longer accurate because a different individual or position has responsibility for the overall operation of the facility, a new authorization satisfying the requirements of paragraph b. of this reporting requirement must be submitted to the Executive Officer prior to or together with any reports, information, or applications to be signed by an authorized representative.

d.	Any person signing a document under paragraph a. or b. of this reporting requirement shall make the following certification:

"I certify under penalty of law that this document and all attachments were prepared under my direction or supervision in accordance with a system designed to assure that qualified personnel properly gather and evaluate the information submitted.  Based on my inquiry of the person or persons who manage the system, or those persons directly responsible for gathering the information, the information submitted is, to the best of my knowledge and belief, true, accurate, and complete.  I am aware that there are significant penalties for submitting false information, including the possibility of fine and imprisonment for knowing violations."

4.	Pursuant to State Board Order No. WQ 84-7, the discharger shall submit with its Report of Waste Discharge for reissuance of its NPDES permit, sufficient information to justify why any effluent proposed to be discharged to the ocean is not being reclaimed for beneficial use.

# 5.	The discharger shall report sewer overflow events in accordance with the following procedures:

a.	A sewer overflow event is a discharge of treated or untreated wastewater at a location not authorized by waste discharge requirements and/or NPDES permit which results from a pump station failure, sewer line break, obstruction, surcharge, or any other operational dysfunction.  Overflows that occur within the treatment plant facility shall be reported to the Regional Board, the Office of Emergency Services (OES) and the County of Orange Health Care Agency, Environmental Health Division, following the procedures listed below.  All sewer overflows within the collection system service area of the treatment facility shall be reported as specified in this Regional Board’s Order No. 96-04, General Waste Discharge Requirements Prohibiting Sanitary Sewer Overflows by Sewage Collection Agencies.  The sewage overflow reporting requirements in this order coincide with the reporting requirements contained in Order No. 96-04.

b.	For the purpose of this permit, discharges to storm drains are considered discharges to surface waters.

c.	The following are the reporting procedures for sewage overflows from sewage treatment and disposal facilities:

(1)	If a sanitary sewer overflow event results in a discharge that is greater than 1,000 gallons or that reaches surface waters, the discharger shall:

(a)	Report the sanitary sewer overflow event to the Regional Board, OES and the County of Orange Health Care Agency, Environmental Health Division by telephone, by voice mail, or by FAX within 24 hours from the time the discharger becomes aware of the sewer overflow event.  This report shall include only the information specified by Item Nos. 1 through 5, 8, 12A, 12B and 13 contained in the Sewer Overflow Report (SOR) form supplied by the Regional Board.

(b)	A SOR form, as well as any additional pertinent information, shall be submitted to the Regional Board no later than five days following the starting date of the sewer overflow event.

(c)	The discharge event shall be included in the next quarterly self-monitoring report, in accordance with the format described in Order No. 96-04.

(2)	If the sanitary sewer overflow event results in a discharge under 1,000 gallons or the discharge does not reach surface waters:

(a)	A report is not required within 24 hours.

(b).	The discharge event shall be included in the next quarterly self-monitoring report, in accordance with the format described in Order No. 96-04.

6.	The discharger shall provide adequate notice to the Executive Officer of the following:

a.	Any new introduction of pollutants into the discharger's treatment works from an indirect discharger which would be subject to Section 301 or 306 of the CWA if it were directly discharging those pollutants;

b.	Any substantial change in the volume or character of pollutants being introduced into the discharger's treatment works by a source introducing pollutants into the treatment works at the time of issuance of this Order; and

c.	For purposes of this paragraph, adequate notice shall include information on:

(1)	The quality and quantity of effluent introduced into the POTW, and

(2)	Any anticipated impact of the change on the quantity or quality of effluent and/or sludge to be discharged from the POTW.

7.	The discharger shall give notice to the Executive Officer as soon as possible of any planned physical alterations or additions to the permitted facility.  Notice is required only when:

a.	The alteration or addition to a permitted facility may meet one of the criteria for determining whether a facility is a new source in 40 CFR Part 122.29(b);

b.	The alteration or addition could significantly change the nature or increase the quantity of pollutants discharged.  This notification applies to pollutants which are not subject to effluent limitations in this Order; or

c.	The alteration or addition results in a significant change in the discharger's sludge use or disposal practices, and such alteration, addition, or change may justify the application of conditions in this Order that are different from or absent in the existing Order, including notification of additional use or disposal sites not reported during the permit application process or not reported pursuant to an approved land application plan.

8.	The discharger shall give advance notice to the Executive Officer of any planned changes in the permitted facility or activity which may result in noncompliance with the requirements of this Order.

9.	This Order is not transferable to any person except after notice to the Executive Officer.  The Executive Officer may require modification or revocation and reissuance of this Order to change the name of the discharger and incorporate such other requirements as may be necessary under the CWA or the California Water Code in accordance with the following:

a.	Transfers by Modification

Except as provided in paragraph b. of this reporting requirement, this Order may be transferred by the discharger to a new owner or operator only if this Order has been modified or revoked and reissued, or a minor modification made to identify the new discharger and incorporate such other requirements as may be necessary under the CWA or California Water Code.

b.	Automatic Transfers

As an alternative to transfers under paragraph a. of this reporting requirement, any NPDES permit may be automatically transferred to a new discharger if:

(1)	The current discharger notifies the Executive Officer at least 30 days in advance of the proposed transfer date in paragraph b.(2) of this reporting requirement;

(2)	The notice includes a written agreement between the existing and new dischargers containing a specific date for transfer of permit responsibility, coverage, and liability between them; and

(3)	The Executive Officer does not notify the existing discharger and the proposed new discharger of his or her intent to modify or revoke and reissue the permit.  A modification under this subparagraph may also be a minor modification under 40 CFR Part 122.63.  If this notice is not received, the transfer is effective on the date specified in the agreement mentioned in paragraph b.(2) of this reporting requirement.

10.	The discharger shall conduct monitoring and submit reports in accordance with Monitoring and Reporting Program (MRP) No. 2000-13.  Monitoring results shall be reported at the intervals specified in MRP No. 2000-13.

- The discharger shall report any noncompliance which may endanger health or the environment.  Any information shall be provided orally to the Executive Officer within 24 hours from the time the discharger becomes aware of the circumstances.  A written submission shall also be provided within 5 days of the time the discharger becomes aware of the circumstances.  A written submission shall contain a description of the noncompliance and its cause; the period of noncompliance, including exact dates and times, and if the noncompliance has not been corrected, the anticipated time it is expected to continue; and steps taken or planned to reduce, eliminate, and prevent recurrence of the noncompliance.  The Executive Officer, or an authorized representative may waive the written report on a case-by-case basis if the oral report has been received within 24 hours.  The following shall be included as information which must be reported within 24 hours under this reporting requirement:

a.	Any unanticipated bypass which exceeds any effluent limitation in this Order;

b.	Any upset which exceeds any effluent limitation in this Order;

c.	Violation of a daily maximum effluent limitation as specified in this Order for the following pollutants:

(1)	Chronic Toxicity

(2)	Arsenic

(3)	Cadmium

(4)	Chromium (Hexavalent)

(5)	Copper

(6)	Lead

(7)	Mercury

(8)	Nickel

(9)	Selenium

(10)	Silver

(11)	Zinc

(12)	Cyanide

(13)	Total Chlorine Residual

(14)	Ammonia

(15)	Phenolic Compounds (non-chlorinated)

(16)	Chlorinated Phenolics

(17)	Endosulfan

(18)	Endrin

(19)	HCH

d.	Any violation of effluent limitations for acute toxicity as specified in this Order;

e.	Any violation of the prohibitions of this Order; and

f.	Any finding of levels of bacteria in a receiving water sample which exceeds bacterial water quality objectives specified in Receiving Water Limitation C.1.a.(1) of this Order.

12.	The discharger shall furnish to the Executive Officer, SWRCB Executive Director, or USEPA, within a reasonable time, any information which the Executive Officer, SWRCB Executive Director, or USEPA may request to determine whether cause exists for modifying, revoking and reissuing, or terminating this Order, or to determine compliance with this Order.  The discharger shall also furnish to the Executive Officer, SWRCB Executive Director, or USEPA, upon request, copies of records required to be kept by this Order.

13.	The discharger shall report all instances of noncompliance not reported under Reporting Requirements G.10, G.11, and G.16 of this Order, at the time monitoring reports are submitted.  The reports shall contain the information listed in Reporting Requirement  G.11 of this Order.

14.	Where the discharger becomes aware that it failed to submit any relevant facts in a Report of Waste Discharge, or submitted incorrect information in a Report of Waste Discharge, or in any report to the Regional Board, it shall promptly submit such facts or information.

15.	Whenever a receiving water sample is found to contain levels of bacteria which exceed bacterial water quality objectives specified in Receiving Water Limitation C.1.a.(1) of this Order, the discharger shall immediately notify the County of Orange Health Care Agency, Environmental Health Division and post signs prohibiting body contact with the water in all areas affected by the contamination.

16.	Reports of compliance or noncompliance with, or any progress reports on, interim and final requirements contained in any compliance schedule of this permit shall be submitted no later than 14 days following each schedule date.

17.	The discharger shall submit a written report to the Executive Officer within 90 days after the average dry weather influent flowrate for any 30-day period equals or exceeds 75 percent of the design capacity of the waste treatment and/or disposal facilities.  The discharger's senior administrative officer shall sign a letter which transmits that report and certifies that the policy-making body is adequately informed about it.  The report shall include:

a.	Average daily flow for the 30-day period, the date on which the instantaneous peak flow occurred, the rate of that peak flow, and the total flow for that day;

b.	The discharger's best estimate of when the average daily dry-weather flowrate will equal or exceed the design capacity of the facilities; and

c.	The discharger's intended schedule for studies, design, and other steps needed to provide additional capacity for the waste treatment and/or disposal facilities and/or control the flowrate before the waste flowrate equals the capacity of present units.

18.	Except for data determined to be confidential under 40 CFR Part 2, all reports prepared in accordance with the terms of this Order shall be available for public inspection at the offices of the California Regional Water Quality Control Board, San Diego Region.  As required by the CWA, Reports of Waste Discharge, this Order, and effluent data shall not be considered confidential.

19.	The discharger shall submit reports and provide notifications to the Regional Board and other agencies as specified in this Order.  These other agencies include USEPA and the County of Orange Health Care Agency, Environmental Health Division.  Reports shall be submitted and notifications shall be made to:

a.		Executive Officer

California Regional Water Quality Control Board

San Diego Region

9771 Clairemont Mesa Boulevard, Suite A

San Diego, California  92124-1324

Phone - (858) 467-2952

Fax - (858) 571-6972

b.	Regional Administrator

U.S. Environmental Protection Agency

Region 9

75 Hawthorne Street

San Francisco, California  94105

c.		County of Orange Health Care Agency

Environmental Health Division

County of Orange

2009 East Edinger Avenue

Santa Ana, CA 92705

Phone (714) 667-3600

Fax (714) 972-0749

d.	Regulatory Unit

Division of Water Quality

State Water Resources Control Board

P.O. Box 944213

Sacramento, CA 94244-2130

H.	NOTIFICATIONS

1.	California Water Code Section 13263(g) states:

No discharge of waste into the waters of the state, whether or not such discharge is made pursuant to waste discharge requirements, shall create a vested right to continue such discharge.  All discharges of waste into waters of the state are privileges, not rights.

2.	The discharger is held accountable for responsibilities, liabilities, legal actions, and penalties as stated in Attachment No. 3 and Attachment No. 5 of this Order.

3.	This Order shall become effective 10 days after the date of its adoption provided the Regional Administrator, USEPA, has no objection.  If the Regional Administrator objects to its issuance, this Order shall not become effective until such objection is withdrawn.

4.	This Order supersedes Order No. 95-01 when this Order becomes effective.

I, John H. Robertus, Executive Officer of the San Diego Regional Water Quality Control Board, do hereby certify the foregoing is a full, true, and correct copy of Order No. 2000-13 adopted by the California Regional Water Quality Control Board, San Diego Region, on February 9, 2000.

_______________

JOHN H. ROBERTUS

Executive Officer

ORDER NO. 2000-13 ENDNOTES

- Secondary treatment is defined by the USEPA Administrator in the Federal Regulations (40 CFR Part 133.100 to 40 CFR Part 133.105) in terms of three parameters: 5-day biochemical oxygen demand (BOD), total suspended solids (TSS), and pH.  Federal regulations allow substitution of 5-day carbonaceous biological demand (CBOD) limitations for BOD limitations.

- Effluent concentration limitations are specified in the 1997 Ocean Plan, Table A.  Mass emission rate (MER) limitations, where applicable, were determined using procedures outlined in the Ocean Plan, equation 2, and a flowrate of 30.0 Mgallons/Day.

- Effluent limitations were determined using the procedures outlined in the 1997 Ocean Plan, and an initial dilution of 109 in the case of no brine discharge, and an initial dilution of 100 in the case of an addition of 1.5 Mgallons/Day of brine wastes to the discharge.  Mass emission rate (MER) limitations were determined using procedures outlined in the Ocean Plan, Equation 2, and a flowrate of 30.0 Mgallons/Day.

- The discharger may, at its option, meet this limitation as a total chromium limitation.

- If the discharger can demonstrate to the satisfaction of the Regional Board (subject to EPA approval) that an analytical method is available to reliably distinguish between strongly and weakly complexed cyanide, effluent limitations for cyanide may be met by the combined measurement of free cyanide, simple alkali metal cyanides, and weakly complexed organometallic cyanide complexes.  In order for the analytical method to be acceptable, the recovery of free cyanide from metal complexes must be comparable to that achieved by Standard Methods 412 F, G, and H (Standard Methods for the Examination of Water and Wastewater, Joint Editorial Board, American Public Health Association, American Water Works Association, and Water Pollution control Federation, most recent edition.)

- The effluent concentration and mass emission rate limitations for total chlorine residual are based on a continuous discharge of chlorine.  Effluent concentration limitations for total chlorine residual, which are applicable to intermittent discharges not exceeding 2 hours, shall be determined through the use of the following equations:

log Co = -0.43 (logx) + 1.8

Ce = Co + Dm(Co – Cs)

where:

Co	=	the concentration (in ug/L) to be met at the completion of

initial dilution

x	=	the duration of uninterrupted chlorine discharge in

minutes

Ce	=	the effluent concentration limitation ug/L to apply when

chlorine is being intermittently discharged

Dm	=	the minimum probable initial dilution

Cs	=	the background seawater concentration	=	0

- Endosulfan shall mean the sum of endosulfan-alpha and –beta and endosulfan sulfate.

- HCH shall mean the sum of the alpha, beta, gamma (lindane) and delta isomers of hexachlorocyclohexane.

- The 1997 Ocean Plan refers to limits specified in Title 17, Division 5, Chapter 4, Group 3, Article 3, Section 32069 of the California code of Regulations.  This section has been repealed, and substituted with limitations set forth in this Order.

- Dichlorobenxenes shall mean the sum of 1,2- and 1,3-dichlorobenzene.

- Chlordane shall mean the sum of chlordane-alpha, chlordane-gamma, chlordene-alpha, chlordene-gamma, nonachlor-alpha, nonachlor-gamma, and oxychlordane.

- DDT shall mean the sum of 4,4’DDT; 2,4’DDT; 4,4’DDE; 2,4’DDE; 4,4’DDD; and 2,4’DDD.

- Halomethanes shall mean the sum of bromoform, bromomethane (methyl bromide), chloromethane (methyl chloride), chlorodibromomethane, and dichlorobromomethane.

- Heptachlor shall mean the sum of heptachlor and heptachlor epoxide.

- PAHs (polynuclear aromatic hydrocarbons) shall mean the sum of acenaphthylene, anthracene, 1,2-benzanthracene, 3,4-benzofluoranthene, benzo[a]pyrene, chrysene, dibenzo[ah]anthracene, fluorene, indeno[1,2,3-cd]pyrene, phenanthrene and pyrene.

- PCBs (polychlorinated biphenyls) shall mean the sum of chlorinated biphenyls whose analytical characteristics resemble those of Aroclor-1016, Aroclor-1221, Aroclor-1232, Aroclor-1242, Aroclor-1248, Aroclor-1254 and Aroclor-1260.

- TCDD EQUIVALENTS shall mean the sum of the concentrations of chlorinated dibenzodioxins (2,3,7,8-CDDs) and chlorinated dibenzofurans (2,3,7,8-CDFs) multiplied by their respective toxicity factors, as shown in the table below.

Isomer Group				Toxicity Equivalence Factor

2,3,7,8-tetra CDD	1.0

2,3,7,8-penta CDD	0.5

2,3,7,8-hexa CDD	0.1

2,3,7,8-hepta CDD	0.01

octa CDD	0.001

2,3,7,8-tetra CDF	0.1

1,2,3,7,8-penta CDF	0.05

2,3,4,7,8 penta CDF	0.5

2,3,7,8 hexa CDFs	0.1

2,3,7,8 hepta CDFs	0.01

octa CDF	0.001