| UNDERGROUND STORAGE TANK MONITORING SYSTEM CERTIFICATION FORM (Page 1 of 6) |
| --- |
| This form must be used to document testing and servicing of underground storage tank (UST) monitoring equipment. A copy of this form must be provided to the UST owner or operator. The owner or operator must submit a copy of this form to the local agency regulating the USTs within 30 days of the date of the monitoring system certification. |
| FACILITY INFORMATION |
| CERS ID | Date of Monitoring System Certification |
| Business Name (Same as Facility Name or DBA – Doing Business As.) | Building # |
| Business Site Address | City | ZIP Code |
| UNDERGROUND STORAGE TANK SERVICE TECHNICIAN INFORMATION |
| Name of Company Performing the Certification | Phone # ( ) - Ext. |
| Mailing Address |
| Name of UST Service Technician Performing the Certification (Print as shown on the ICC Certification.) |
| Contractor/Tank Tester License # | ICC Certification # | ICC Certification Expiration Date |
| Monitoring System Training and Certifications (List all applicable certifications.) | Expiration Date |
| Results of Testing/Servicing |
| Indicate and attach the following reports if the monitoring equipment is capable of generating either. | Y | N | NA |
| Monitoring System Set-up | Alarm History Report |  |  |  |
| Was any monitoring equipment replaced? (If “Yes,” identify the specific devices replaced and list the manufacturer and model for all replacement parts in section IV below.) |  |  |  |
| Was damage, debris, or liquid found inside any secondary containment systems? (If “Yes,” describe what was found in section IV below.) |  |  |  |
| Is all monitoring equipment operational per manufacturer’s specifications? (If “No,” describe why in section IV below.) |  |  |  |
| COMMENTS |
| If directed to use this section, describe how and when the issues were or will be corrected. |
| CERTIFICATION BY UST service technician conducting this TESTING |
| I hereby certify that the equipment identified in this document was inspected/serviced in accordance with California Code of Regulations, title 23, division 3, chapter 16, section 2638 and all information contained herein is true and accurate. Attached to this certification is information (e.g., manufacturers' checklists, monitoring system set-up, alarm history report, etc.) necessary to verify that this information and the site plan showing the layout of UST system is complete and accurate. |
| UST Service Technician Signature |

| UNDERGROUND STORAGE TANK MONITORING SYSTEM CERTIFICATION FORM (Page 2 of 6) |
| --- |
| INVENTORY OF EQUIPMENT CERTIFIED |
| A separate Monitoring System Certification Form must be prepared for each monitoring system control panel. |
| Make of Monitoring System Control Panel | Model of Monitoring System Control Panel | Software Version Installed |
| Check the appropriate boxes to indicate specific equipment inspected/serviced. |
| Monitoring Device Used | Device Model # | Monitoring Device Used | Device Model # |
| Tank ID: (By tank number, stored product, etc.) | Tank ID: (By tank number, stored product, etc.) |
| In-tank Gauging (SW Tank) |  | In-tank Gauging (SW Tank) |  |
| Annular Space or Vault Sensor |  | Annular Space or Vault Sensor |  |
| VPH Sensor |  | VPH Sensor |  |
| Product Piping | Product Piping |
| Mechanical LLD |  | Mechanical LLD |  |
| Electronic LLD |  | Electronic LLD |  |
| VPH Sensor (Piping) |  | VPH Sensor (Piping) |  |
| Sump Sensor |  | Sump Sensor |  |
| VPH Sensor (Sump) |  | VPH Sensor (Sump) |  |
| Fill Piping | Fill Piping |
| VPH Sensor (Piping) |  | VPH Sensor (Piping) |  |
| Sump Sensor |  | Sump Sensor |  |
| VPH Sensor (Sump) |  | VPH Sensor (Sump) |  |
| Vent Piping | Vent Piping |
| VPH Sensor (Piping) |  | VPH Sensor (Piping) |  |
| Sump Sensor |  | Sump Sensor |  |
| VPH Sensor (Sump) |  | VPH Sensor (Sump) |  |
| Vapor Recovery Piping | Vapor Recovery Piping |
| VPH Sensor (Piping) |  | VPH Sensor (Piping) |  |
| Sump Sensor |  | Sump Sensor |  |
| VPH Sensor (Sump) |  | VPH Sensor (Sump) |  |
| Monitoring Device Used | Device Model # | Monitoring Device Used | Device Model # |
| Tank ID: (By tank number, stored product, etc.) | Tank ID: (By tank number, stored product, etc.) |
| In-tank Gauging (SW Tank) |  | In-tank Gauging (SW Tank) |  |
| Annular Space or Vault Sensor |  | Annular Space or Vault Sensor |  |
| VPH Sensor |  | VPH Sensor |  |
| Product Piping | Product Piping |
| Mechanical LLD |  | Mechanical LLD |  |
| Electronic LLD |  | Electronic LLD |  |
| VPH Sensor (Piping) |  | VPH Sensor (Piping) |  |
| Sump Sensor |  | Sump Sensor |  |
| VPH Sensor (Sump) |  | VPH Sensor (Sump) |  |
| Fill Piping | Fill Piping |
| VPH Sensor (Piping) |  | VPH Sensor (Piping) |  |
| Sump Sensor |  | Sump Sensor |  |
| VPH Sensor (Sump) |  | VPH Sensor (Sump) |  |
| Vent Piping | Vent Piping |
| VPH Sensor (Piping) |  | VPH Sensor (Piping) |  |
| Sump Sensor |  | Sump Sensor |  |
| VPH Sensor (Sump) |  | VPH Sensor (Sump) |  |
| Vapor Recovery Piping | Vapor Recovery Piping |
| VPH Sensor (Piping) |  | VPH Sensor (Piping) |  |
| Sump Sensor |  | Sump Sensor |  |
| VPH Sensor (Sump) |  | VPH Sensor (Sump) |  |

| UNDERGROUND STORAGE TANK MONITORING SYSTEM CERTIFICATION FORM (Page 3 of 6) |
| --- |
| Monitoring Device Used | Device Model # | Monitoring Device Used | Device Model # |
| Vent/Transition Sump ID: | Vent/Transition Sump ID: |
| Sump Sensor |  | Sump Sensor |  |
| VPH Sensor |  | VPH Sensor |  |
| UDC ID: | UDC ID: |
| Electronic Sensor |  | Electronic Sensor |  |
| Mechanical Device |  | Mechanical Device |  |
| VPH Sensor |  | VPH Sensor |  |
| UDC ID: | UDC ID: |
| Electronic Sensor |  | Electronic Sensor |  |
| Mechanical Device |  | Mechanical Device |  |
| VPH Sensor |  | VPH Sensor |  |
| UDC ID: | UDC ID: |
| Electronic Sensor |  | Electronic Sensor |  |
| Mechanical Device |  | Mechanical Device |  |
| VPH Sensor |  | VPH Sensor |  |
| UDC ID: | UDC ID: |
| Electronic Sensor |  | Electronic Sensor |  |
| Mechanical Device |  | Mechanical Device |  |
| VPH Sensor |  | VPH Sensor |  |
| Other Monitored Component ID: | Other Monitored Component ID: |
| Other (Specify in section VII.) |  | Other (Specify in section VII.) |  |
| Other Monitored Component ID: | Other Monitored Component ID: |
| Other (Specify in section VII.) |  | Other (Specify in section VII.) |  |
| Other Monitored Component ID: | Other Monitored Component ID: |
| Other (Specify in section VII.) |  | Other (Specify in section VII.) |  |
| Include information for every underground storage tank component monitored by this monitoring system control panel. If the monitoring system control panel monitors more components than this form accommodates, additional copies of these pages may be attached. |
| COMMENTS |
| Use this section to provide any additional comments about the inventory of the equipment certified. |

| UNDERGROUND STORAGE TANK MONITORING SYSTEM CERTIFICATION FORM (Page 4 of 6) |
| --- |
| Monitoring System and Programming |
| This section must be completed if a monitoring panel is used to perform leak detection monitoring. | Y | N | NA |
| Are the visual and audible alarms operational? |  |  |  |
| Were all sensors visually inspected for kinks and breaks in the cables and for residual buildup to ensure that floats move freely, functionally tested, and confirmed operational? |  |  |  |
| Were all sensors installed at lowest point of secondary containment and positioned so that other equipment will not interfere with their proper operation? |  |  |  |
| Was monitoring system set-up reviewed to ensure proper settings? |  |  |  |
| Was the monitoring panel’s backup battery visually inspected, functionally tested, and confirmed operational? |  |  |  |
| Does the flow of fuel stop at the dispenser if a leak is detected in the under-dispenser containment? |  |  |  |
| Does the turbine automatically shut down if the piping secondary containment monitoring system fails to operate or is electrically disconnected? |  |  |  |
| Does the turbine automatically shut down if the piping secondary containment monitoring system detects a leak? |  |  |  |
| Which sensors initiate positive shut down? (Check all that apply.) | Sump | Under-dispenser containment |  |  |  |
| If alarms are relayed to a remote monitoring station, is all communications equipment (e.g. modem) operational? |  |  |  |
| For any answer of “N” above, describe in section IX how and when these deficiencies were or will be corrected. |
| COMMENTS |
| In-Tank Gauging Testing |
| Check this box if tank gauging is used only for inventory control. (Do not complete this section.) | Y | N | NA |
| Check this box if NO tank gauging equipment is installed. (Do not complete this section.) |  |  |  |
| This section must be completed if in-tank gauging is used to perform leak detection monitoring. |  |  |  |
| Has all input wiring been inspected for kinks and breaks in the cables and for proper entry and termination, including testing for ground faults? |  |  |  |
| Were all in-tank gauging probes visually inspected for damage and residue buildup to ensure that floats move freely, functionally tested, and confirmed operational? |  |  |  |
| Was accuracy of system’s product level readings tested? |  |  |  |
| Was accuracy of system’s water level readings tested? |  |  |  |
| Were all probes reinstalled properly? |  |  |  |
| Were all items on the equipment manufacturer’s maintenance checklist completed? |  |  |  |
| For any answer of “N” above, describe in section XI how and when these deficiencies were or will be corrected. |
| COMMENTS |
| UNDERGROUND STORAGE TANK MONITORING SYSTEM CERTIFICATION FORM (Page 5 of 6) |
| Line Leak Detector TESTING |
| Check this box if line leak detectors (LLD) are NOT installed. (Do not complete this section.) | Y | N | NA |
| This section must be completed if LLDs are installed. |  |  |  |
| Was a leak simulated to verify LLD performance? |  |  |  |
| (Check all that apply.) Simulated leak rate verified: | 3 GPH | 0.1 GPH | 0.2 GPH |  |  |  |
| Was the testing apparatus properly calibrated? |  |  |  |
| For emergency generator tank systems, does the LLD create an audible and visual alarm when a leak is detected? |  |  |  |
| For mechanical LLDs, does the LLD restrict the flow through the pipe when a leak is detected? |  |  |  |
| For electronic LLDs, does the turbine automatically shut off when a leak is detected? |  |  |  |
| For electronic LLDs, does the turbine automatically shut off if any portion of the monitoring system is disabled or disconnected? |  |  |  |
| For electronic LLDs, does the turbine automatically shut off if any portion of the monitoring system malfunctions or fails a test? |  |  |  |
| For electronic LLDs, have all accessible wiring connections been visually inspected for kinks and breaks? |  |  |  |
| Were all items on the equipment manufacturer’s maintenance checklist completed? |  |  |  |
| Were all LLDs confirmed operational within regulatory requirements? |  |  |  |
| For any answer of “N” above, describe in section XIII how and when these issues were or will be corrected. |
| COMMENTS |
| Vacuum / Pressure/ Hydrostatic Monitoring Equipment Testing |
| Check this box if VPH monitoring is NOT used. (Do not complete this section.) |
| This section must be completed if VPH monitoring is used to perform leak detection monitoring. |
| System Type (Mark all that apply.) | Vacuum | Pressure | Hydrostatic |
| Sensor ID | Component(s) Monitored by this Sensor | Sensor Functionality Test | Interstitial Communication Test |
|  |  | Pass | Fail | Pass | Fail |
|  |  | Pass | Fail | Pass | Fail |
|  |  | Pass | Fail | Pass | Fail |
|  |  | Pass | Fail | Pass | Fail |
|  |  | Pass | Fail | Pass | Fail |
|  |  | Pass | Fail | Pass | Fail |
|  |  | Pass | Fail | Pass | Fail |
|  |  | Pass | Fail | Pass | Fail |
|  |  | Pass | Fail | Pass | Fail |
|  |  | Pass | Fail | Pass | Fail |
|  |  | Pass | Fail | Pass | Fail |
|  |  | Pass | Fail | Pass | Fail |
| How was interstitial communication verified? | Simulated leak at far ends of the interstitial space. | Visual Inspection |
|  | Other (Describe the method in section XV below.) | Gauge |
| Was the vacuum or pressure restored to operating levels in all interstitial spaces? | Yes | No (Describe the reason in section XV below.) |
| For any answer of “FAIL” above, describe in section XV how and when these issues were or will be corrected. |
| COMMENTS |

| UNDERGROUND STORAGE TANK MONITORING SYSTEM CERTIFICATION FORM (Page 6 of 6) |
| --- |
| Monitoring Site Plan |
| Date site map was prepared: |
| If you already have a site plan that shows all required information, you may include it, rather than this page, with your Monitoring System Certification Form. The site plan must show the general layout of tanks and piping and clearly identify locations of the following equipment, if installed: 1) monitoring system control panels; 2) in-tank liquid level probes (if used for leak detection); 3) devices monitoring tank annular spaces or vault; 4) devices monitoring product piping; 5) devices monitoring fill piping; 6) devices monitoring vent piping; 7) devices monitoring vapor recovery piping; 8) devices monitoring vent/transition sumps; 9) devices monitoring under-dispenser containment; 10) line leak detectors; and 11) devices monitoring any other secondary containment areas. |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | LEGEND |